## Instructions
Contains Confidential Information Including Privileged and Critical Energy Infrastructure Information. Do Not Distribute. Attachment C - Data Sampling Request | [5 empty] | Updated: 9/21/2020
Standard Number | Requirement Number | Data List | Data List returned to ReliabilityFirst | Evidence Requested | Evidence Returned to ReliabilityFirst
PRC-005-6 | R3. | Provide a list of all Components of Protection Systems specified in PRC-005-6 Applicability Section 4.2 that are part of a time-based maintenance program. For each of the Components, provide: - substation/generation station - maintenance and testing interval(s) - test dates. Use Attached Templates | Return Data List to ReliabilityFirst 55 business days prior to the start of the scheduled audit. | Provide evidence that Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components included within its time-based program in accordance with Requirement R3 have been maintained. The evidence may include, but is not limited to, dated maintenance records, dated maintenance summaries, dated check-off lists, dated inspection records, or dated work orders. | Return evidence to ReliabilityFirst no later than 30 business days prior to the start of the scheduled audit.

## PRC-005-6 R3-Relays, etc.
Index Number (RF use only) | Function (DP/GO/ TO) | Generating Station/ Substation | Component Type (See Drop-Down box) | Microprocessor Relay (Yes / No / N/A) | Component is part of a UFLS, UVLS, RAS (SPS), Auto Recl or Sudden Pressure Relaying (Blank if no) | List of all applicable Components* | Device Identifier (if applicable) | Defined maintenance and testing Interval(s) per prior Standard/ Version ** | Defined maintenance and testing Interval(s) per PRC-005-2/6, R3 or R4. | Previous Test Date | Date Last Maintained/Tested | Due Date for next Maintenance and Testing | Last maintained / tested under | [5 empty] | PRC-005-2/6 Table ***** (if applicable) | PRC-005-2/6 Table Row ****** (if applicable) | Comments (please provide any comments that you feel are relevant) | Notes: * Alternative - List relays only. RF will select sample. Entity will provide requested evidence for all components associated with selected relays. ** PRC-005-1.1 R1.1, PRC-008-0 R1, PRC-011-0 | Valid_Components | Protective Relay | Communications System | Current Sensing Device | Voltage Sensing Device | Control Circuitry |  | UFLS | UVLS | RAS | Auto Reclosing | Sudden Pressure | Yes | No | N/A
[13 empty] | PRC-005-1.1b (X/Blank) | PRC-008-0 (X/Blank) | PRC-011-0 (X/Blank) | PRC-017-0 (X/Blank) | PRC-005-2/6 Time Based (X/Blank) | PRC-005-2/6 Performance Based (X/Blank) | [7 empty] | Valid_Components | Protective Relay | Communications System | Current Sensing Device | Voltage Sensing Device | Control Circuitry | UFLS | UVLS | RAC (SPS)
| GO | Gen A | Protective Relay | Yes |  | U2 GSU Diff | 1682 | 4 Years | 6 Years | 2011-06-10 | 2015-06-01 | 2021-06-01 |  |  |  |  | X |  | 1-1 | 1 | Example | R1.1.1-R1.1.4 or PRC-017-0 R1.1.1-R1.1.4
| DP | Substation D | Protective Relay | No |  | Brk 1-2 Fail | 10753 | 5 Years | 6 Years | 2009-11-06 | 2014-11-02 | 2020-11-02 |  |  |  |  | X |  | 1-1 | 1 | Example | *** 4/1/2019 or 4/1/2021
| TO | Substation D | Protective Relay | Yes |  | Line 13825 | 12835 | 12 Years | 12 Years | 2003-11-06 | 2014-08-02 | 2026-08-02 | X | [5 empty] | 1-1 | 3 | Example | as per Implementation Plan for
| TO | Substation D | Communications System | N/A |  | Line 13825 | 18268 | 1 Year | 4 Months | 2017-12-03 | 2018-04-01 | 2018-08-01 |  |  |  |  | X |  | 1-2 | 1 | Example | intervals consistent with applicable Table
| TO | Substation D | Communications System | N/A |  | Line 13825 | 18268 |  | 6 Years | N/A | N/A | 4/1/2021*** | N/A | [5 empty] | 1-2 | 2 | Example | or next due date under PRC-005-1,
| TO | Substation D | Current Sensing Device | N/A |  | Line 13825 A | 16325 | 10 Years | None | 2004-09-01 | 2014-08-02 | N/A | X | [5 empty] | 1-3 | 2 | Continuously verified | whichever is earlier.
| DP | Substation E | Protective Relay | Yes | UFLS | Fdr 103 | 34812 | 5 Years | 6 Years | 2009-03-05 | 2014-01-08 | 1/8/2019*** |  | X |  |  |  |  | 3 | 1 | Example | **** 4/1/2019, 4/1/2023 or 4/1/2027
| DP | Substation E | Voltage Sensing Device | N/A | UVLS | Fdr 104 B | 24897 | 10 Years | 12 Years | 2004-03-02 | 2014-01-08 | 1/8/2024**** |  |  | X |  |  |  | 3 | 4 | Example | as per Implementation Plan for
| TO | Substation F | Control Circuitry | N/A | RAS | Bus 1 B | 43572 | 5 Years | 12 Years | 2009-02-20 | 2014-02-07 | 2/7/2019**** |  |  |  | X |  |  | 1-5 | 4 | Example | intervals consistent with applicable Table
| TO | Substation F | Control Circuitry | N/A | Sudden Pressure | Tr 1 | 37465 |  | 12 Years |  | 2015-09-29 | 2027-09-29 |  |  |  |  | X |  | 5 | 3 | Example | or next due date under PRC-005-1,
whichever is earlier.
***** Identify the specific table and row of
PRC-005-2/6, Table 1-1, 1-2, 1-3, Table 2, or
Table 3 under which the Component is
being maintained.
****** Count the row under the Maximum
Maintenance Interval column. May be left
blank if not yet maintained under PRC-005-2/6.