## General
PRC-005 Maintenance Tables Each tab corresponds to a table in PRC-005-6 and provides a tool to identify where in Protection System maintence records each required maintencae activity is documented.
References
PRC-005-6 Standard (including maintenance tables) | http://www.nerc.com/pa/Stand/Reliability%20Standards/PRC-005-6.pdf
PRC-005-6 Implementation Plan | http://www.nerc.com/pa/Stand/PRC0056RD/PRC-005-6_Implementation_Plan_clean_2015Oct09.pdf
Supplmental Reference and FAQ | http://www.nerc.com/pa/Stand/PRC0056RD/Supplementary_Reference_Rev_2015Oct09_clean.pdf
FERC Order RD16-2-000 | http://www.nerc.com/FilingsOrders/us/FERCOrdersRules/Letter%20Order%20Approving%20PRC-005-6.pdf
RSAW | http://www.nerc.com/pa/comp/Reliability%20Standard%20Audits%20Worksheets%20DL/RSAW%20PRC-005-6_2016_V3.docx
Version Date
1 4/16/2018

## Table 1-1
| Table 1-1 Component Type - Protective Relay: Unmonitored Microprocessor Relays Excluding distributed UFLS and distributed UVLS (see Table 3) In boxes provided, site document and page number pointing to the evidence of testing. | [8 empty] | Table 1-1 Component Type - Protective Relay: Unmonitored non-microprocessor relays Excluding distributed UFLS and distributed UVLS (see Table 3) In boxes provided, site document and page number pointing to the evidence of testing. | [7 empty] | Table 1-1 Component Type - Protective Relay Excluding distributed UFLS and distributed UVLS (see Table 3) Monitored Microprocessor relays with the following: •Internal self-diagnosis and alarming •Voltage and/or current waveform sampling three or more times per power cycle, and conversion of samples to numeric values... •Alarming for power supply failure In boxes provided, site document and page number pointing to the evidence of testing. | [9 empty] | Table 1-1 Component Type - Protective Relay Excluding distributed UFLS and distributed UVLS (see Table 3) Monitored Microprocessor relays with the following: •Internal self-diagnosis and alarming •Voltage and/or current waveform sampling three or more times per power cycle and conversion of samples to numeric values... •Alarming for power supply failure •AC measures and continuously verified by comparison to an idependent ac measurement source, with alarming for excessive error •Some or all binary or status inputs and control outputs are monitored by a process that continuously demonstrates ability to perform as designed, with alarming for failure •Alarming for change of settings In boxes provided, site document and page number pointing to the evidence of testing.
RF Index Number | Generating Station/ Substation | Component Description (e.g. which Transformer, Line, or Bus does it protect; type, function of relay; primary or backup) | Device Identifier (if applicable) | 6 Calendar Years Any unmonitored protective relay not having all the monitoring attributes of a Monitoring in Table 2 |  |  |  |  | RF Index Number | Generating Station/ Substation | Component Description (e.g. which Transformer, Line, or Bus does it protect; type, function of relay; primary or backup) | Device Identifier (if applicable) | 6 Calendar Years Any unmonitored protective relay not having all the monitoring attributes of a Monitoring in Table 2 |  |  |  | RF Index Number | Generating Station/ Substation | Component Description (e.g. which Transformer, Line, or Bus does it protect; type, function of relay; primary or backup) | Device Identifier (if applicable) | Has attributes for extending interval | 12 Calendar Years Monitored protective relays having the attributes in Table 2 |  |  |  |  | RF Index Number | Generating Station/ Substation | Component Description (e.g. which Transformer, Line, or Bus does it protect; type, function of relay; primary or backup) | Device Identifier (if applicable) | Has attributes for extending interval | 12 Calendar Years Monitored protective relays having the attributes in Table 2
RF Index Number |  |  |  | Latest Test Date: | For all unmonitored relays: •Verify that settings are as specified | For microprocessor relays: •Verify operation of the relay inputs and outputs that are essential to proper functioning of the Protection System. | For microprocessor relays: •Verify acceptable measurement of power system input values. | Comments if applicable: | RF Index Number |  |  |  | Latest Test Date: | For all unmonitored relays: •Verify that settings are as specified | For non-microprocessor relays: •Test and, if necessary calibrate | Comments if applicable: | RF Index Number |  |  |  |  | Latest Test Date: | For monitored relays: •Verify that settings are as specified | For monitored relays: •Operation of the relay inputs and outputs that are essential to proper function of the Protection System | For monitored relays: •Acceptable measurement of power system input values | Comments if applicable: | RF Index Number |  |  |  |  | Latest Test Date: | For monitored relays: •Verify only the unmonitored relay inputs and outputs that are essential to proper functioning of the Protection System | Comments if applicable:

## Table 1-2
Table 1-2 Component Type - Communications Systems Excluding distributed UFLS and distributed UVLS (see Table 3) In boxes provided, site document and page number pointing to the evidence of testing. (If these relays do not have communication systems - just type N/A)
RF Index Number | Generating Station/ Substation | Component Description (e.g. for what Relay(s) does it provide communication; primary or backup,etc.) | Device Identifier (if applicable) | 4 Calendar Months-Last Test Date Any unmonitored communications system necessary for correct operation of protective functions, and not having all the monitoring attributes of a category below. |  |  | 4 Calendar Months- Previous Test Date 1 Any unmonitored communications system necessary for correct operation of protective functions, and not having all the monitoring attributes of a category below. |  |  | 4 Calendar Months- Previous Test Date 2 Any unmonitored communications system necessary for correct operation of protective functions, and not having all the monitoring attributes of a category below. |  |  | 4 Calendar Months- Previous Test Date 3 Any unmonitored communications system necessary for correct operation of protective functions, and not having all the monitoring attributes of a category below. |  |  | 6 Calendar Years Any unmonitored communications system necessary for correct operation of protective functions, and not having all the monitoring attributes of a category below. |  |  |  | 12 Calendar Years Any communications system with continuous monitoring or periodic automated testing for the presence of the channel function, and alarming for loss of function (See Table 2). |  |  |  | 12 Calendar Years Any communications system with all of the following: • Continuous monitoring or periodic automated testing for the performance of the channel using criteria pertinent to the communications technology applied (e.g. signal level, reflected power, or data error rate, and alarming for excessive performance degradation). (See Table 2) • Some or all binary or status inputs and control outputs are monitored by a process that continuously demonstrates ability to perform as designed, with alarming for failure (See Table 2).
RF Index Number |  |  |  | Test Date: | Verify that the communications system is functional. | Comments: | Test Date: | Verify that the communications system is functional. | Comments: | Test Date: | Verify that the communications system is functional. | Comments: | Test Date: | Verify that the communications system is functional. | Comments: | Test Date: | Verify that the communications system meets performance criteria pertinent to the communications technology applied (e.g. signal level, reflected power, or data error rate). | Verify operation of communications system inputs and outputs that are essential to proper functioning of the Protection System. | Comments: | Test Date: | Verify that the communications system meets performance criteria pertinent to the communications technology applied (e.g. signal level, reflected power, or data error rate). | Verify operation of communications system inputs and outputs that are essential to proper functioning of the Protection System. | Comments: | Test Date: | Verify only the unmonitored communications system inputs and outputs that are essential to proper functioning of the Protection System | Comments:

## Table 1-3
Table 1-3 Component Type - Voltage and Current Sensing Devices Providing Inputs to Protective Relays Excluding distributed UFLS and distributed UVLS (see Table 3) In boxes provided, site document and page number pointing to the evidence of testing.
RF Index Number | Generating Station/ Substation | Component Description (e.g. to which Relay(s) does it provide an input or which Transformer, Line, or Bus phase does it monitor) | Device Identifier |  | 12 Calendar Years Any voltage and current sensing devices not having monitoring attributes of the category below.
RF Index Number |  |  |  | PT or CT | Test Date: | Verify that current and voltage signal values are provided to the protective relays. | Comments:

## Table 1-4
Table 1-4 Component Type - Protection System Station DC Supply Excluding distributed UFLS and distributed UVLS (see Table 3)
4 Calendar Months Provide evidence of testing for last battery test plus 3 previous tests (4 total tests). In boxes provided, site document and page number pointing to the evidence of testing.
RF Index Number | Generating Station/ Substation | Battery | Table Used (e.g. 1-4a, 1-4b, 1-4c) | Last Test Date |  |  |  |  | Previous Test 1 |  |  |  |  | Previous Test 2 |  |  |  |  | Previous Test 3
RF Index Number |  |  |  | Test Date: | Verify: • Station dc supply voltage | Inspect: • Electrolyte level | Inspect: • For unintentional grounds | Comments: | Test Date: | Verify: • Station dc supply voltage | Inspect: • Electrolyte level | Inspect: • For unintentional grounds | Comments: | Test Date: | Verify: • Station dc supply voltage | Inspect: • Electrolyte level | Inspect: • For unintentional grounds | Comments: | Test Date: | Verify: • Station dc supply voltage | Inspect: • Electrolyte level | Inspect: • For unintentional grounds | Comments:
Table 1-4 Component Type - Protection System Station DC Supply Excluding distributed UFLS and distributed UVLS (see Table 3)
18 Calendar Months Provide Evidence of Testing for Previous and Last Test date (two total tests). In boxes provided, site document and page number pointing to the evidence of testing.
RF Index Number | Generating Station/ Substation | Battery | Table Used (e.g. 1-4a, 1-4b, 1-4c) | Last Test Date | [7 empty] | Previous Test Date
RF Index Number |  |  |  | Test Date: | Verify: • Float voltage of battery charger | Verify: • Battery continuity | Verify: • Battery terminal connection resistance | Verify: • Battery intercell or unit-to-unit connection resistance | Inspect: • Cell condition of all individual battery cells where cells are visible – or measure battery cell/unit internal ohmic values where the cells are not visible | Inspect: • Physical condition of battery rack | Comments: | Test Date: | Verify: • Float voltage of battery charger | Verify: • Battery continuity | Verify: • Battery terminal connection resistance | Verify: • Battery intercell or unit-to-unit connection resistance | Inspect: • Cell condition of all individual battery cells where cells are visible – or measure battery cell/unit internal ohmic values where the cells are not visible | Inspect: • Physical condition of battery rack | Comments:
Table 1-4 Component Type - Protection System Station DC Supply Excluding distributed UFLS and distributed UVLS (see Table 3)
18 Calendar Months or 6 Calendar Years Provide Previous Test Date and Evidence of Testing. In boxes provided, site document and page number pointing to the evidence of testing.
RF Index Number | Generating Station/ Substation | Battery | Table Used (e.g. 1-4a, 1-4b, 1-4c) |  | 18 Calendar Months | 6 Calendar Years
RF Index Number |  |  |  | Test Date: | Verify that the station battery can perform as manufactured by evaluating cell/unit measurements indicative of battery performance (e.g. internal ohmic values or float current) against the station battery baseline. | OR Verify that the station battery can perform as manufactured by conducting a performance or modified performance capacity test of the entire battery bank. | Comments:

## Table 1-5
Table 1-5 Component Type – Control Circuitry Associated with Protective Functions Excluding distributed UFLS and distributed UVLS (see Table 3) In boxes provided, site document and page number pointing to the evidence of testing.
RF Index Number | Generating Station/ Substation | Component Description (e.g. for what relay(s) it provides an input) | Device Identifier (if applicable) | 6 Calendar Years Trip coils or actuators of circuit breakers, interrupting devices, or mitigating devices (reglardless of any monitoring of the control circuitry). |  |  | 6 Calendar Years Electromechanical lockout devices which are directly in a trip path from the protective relay to the interrupting device trip coil (regardless of any monitoring of the control circuitry). |  |  | 12 Calendar Years Unmonitored control circuitry associated with protective functions inclusive of all auxiliary relays. |  |  | 12 Calendar Years Unmonitored control circuitry associated with RAS
RF Index Number |  |  |  | Latest Test Date: | Verify that each trip coil is able to operate the circuit breaker, interrupting device, or mitigating device. | Comments: | Latest Test Date: | Verify electrical operation of electromechanical lockout devices. | Comments: | Latest Test Date: | Verify all paths of the trip circuits inclusive of all auxiliary relays through the trip coil(s) of the circuit breakers or other interrupting devices. | Comments: | Latest Test Date: | Verify all paths of the control circuits essential for proper operation of the RAS | Comments:

## Table 2
Table 2 Alarming Paths and Monitoring In Tables 1-1 through 1-5, Table 3, Tables 4-1 through 4-3, and Table 5 alarm attributes used to justify extended maximum maintenance intervals and/or reduced maintenance activites are subject to the following maintenance requirements In boxes provided, site document and page number pointing to the evidence of testing.
RF Index Number | Generating Station/ Substation | Component Description (e.g. what does it alarm or monitor) | Device Identifier (if applicable) | 12 Calendar Years Any alarm path through which alarms in Tables 1-1 through 1-5, Table 3, Tables 4-1 through 4-3, and Table 5 are conveyed from the alarm origin to the location where corrective action can be initiated, and not having all the attributes of the “Alarm Path with monitoring” category below. Alarms are reported within 24 hours of detection to a location where corrective action can be initiated.
RF Index Number |  |  |  | Test Date: | Verify that the alarm path conveys alarm signals to a location where corrective action can be initiated. | Comments:

## Table 3
Table 3 Maintenance Activities and Intervals for distributed UFLS and distributed UVLS In boxes provided, site document and page number pointing to the evidence of testing. If the test is not applicable (e.g. microprocessor relays need not be calibrated) just type N/A
RF Index Number | Generating Station/ Substation | Component Description (e.g., what does it trip) | Type (UFLS or UVLS, microprocessor or non-microprocessor) | Device Identifier (if applicable) | 6 Calendar Years Any unmonitored protective relay not having all the monitoring attributes of a category below. | [5 empty] | 12 Calendar Years Monitored microprocessor protective relay with the following: • Internal self-diagnosis and alarming (See Table 2). • Voltage and/or current waveform sampling three or more times per power cycle, and conversion of samples to numeric values for measurement calculations by microprocessor electronics. • Alarming for power supply failure (See Table 2). |  |  |  |  | 12 Calendar Years Monitored microprocessor protective relay with the following: • Internal self-diagnosis and alarming (See Table 2). • Voltage and/or current waveform sampling three or more times per power cycle, and conversion of samples to numeric values for measurement calculations by microprocessor electronics. • Alarming for power supply failure (See Table 2). • AC measurements are continuously verified by comparison to an independent ac measurement source, with alarming for excessive error (See Table 2). • Some or all binary or status inputs and control outputs are monitored by a process that continuously demonstrates ability to perform as designed, with alarming for failure (See Table 2). • Alarming for change of settings (See Table 2). |  |  | 12 Calendar Years Voltage and/or current sensing devices associated with UFLS or UVLS systems. |  |  |  | 12 Calendar Years Protection System dc supply for tripping non-BES interrupting devices used only for a UFLS or UVLS system. |  |  | 12 Calendar Years Control circuitry between the UFLS or UVLS relays and electromechanical lockout and/or tripping auxiliary devices (excludes non-BES interrupting device trip coils). |  |  | 12 Calendar Years Electromechanical lockout and/or tripping auxiliary devices associated only with UFLS or UVLS systems (excludes non-BES interrupting device trip coils).
RF Index Number |  |  |  |  | Latest Test Date: | Verify that settings are as specified. | For non-microprocessor relays: • Test and, if necessary calibrate | For microprocessor relays: • Verify operation of the relay inputs and outputs that are essential to proper function of the Protection System | For microprocessor relays: • verify acceptable measurement of power system input values | Comments: | Latest Test Date: | Verify • Settings are as specified | Verify • Operation of the relay inputs and outputs that are essential to proper function of the Protection System | Verify • Acceptable measurement of power system input values | Comments: | Latest Test Date: | Verify only the unmonitored relay inputs and outputs that are essential to proper functioning of the Protection System. | Comments: | Latest Test Date: | Device Identifier (PT and/or CT) | Verify that current and/or voltage signal values are provided to the protective relays. | Comments: | Test Date: | Verify Protection System dc supply voltage. | Comments: | Test Date: | Verify the path from the relay to the lockout and/or tripping auxiliary relay (including essential supervisory logic). | Comments: | Test Date: | Verify electrical operation of electromechanical lockout and/or tripping auxiliary devices. | Comments:

## Table 4-1
Table 4-1 Maintenance Activities and Intervals for Automatic Reclosing Components Compontent Type - Reclosing and Suervisory Relays In boxes provided, site document and page number pointing to the evidence of testing. If the test is not applicable (e.g. microprocessor relays need not be calibrated) just type N/A
RF Index Number | Generating Station/ Substation | Component Description (e.g., what does it protect?) | Device Identifier (if applicable) | 6 Calendar Years Any unmonitored protective relay not having all the monitoring attributes of a category below. | [5 empty] | 12 Calendar Years Monitored microprocessor reclosing relay or supervisory relay with the following: • Internal self-diagnosis and alarming (See Table 2). • Alarming for power supply failure (See Table 2). For supervisory relay: • Voltage waveform sampling three or more times per power cycle, and conversion of samples to numeric values for measurement calculations by microprocessor electronics. |  |  |  |  | 12 Calendar Years Monitored microprocessor protective relay with the following: • Internal self-diagnosis and alarming (See Table 2). • Alarming for power supply failure (See Table 2). •Some or all binary or status inputs and control outputs are monitored by a process that continuously demonstrates ability to perform as designed, with alarming for failure (See Table 2). •Alarming for change of settings (See Table 2) For supervisory relay: • Voltage waveform sampling three or more times per power cycle, and conversion of samples to numeric values for measurement calculations by microprocessor electronics. • AC measurements are continuously verified by comparison to an independent ac measurement source, with alarming for excessive error (See Table 2).
RF Index Number |  |  |  | Test Date: | Verify that settings are as specified. | For non-microprocessor relays or supervisor relays: • Test and, if necessary calibrate | For microprocessor relays or supervisory relays: • Verify operation of the relay inputs and outputs that are essential to proper functioning of the Automatic Reclosing | For microprocessor relays: • verify acceptable measurement of power system input values | Comments: | Test Date: | Verify • Settings are as specified | Verify • Operation of the relay inputs and outputs that are essential to proper functioning of the Automatic Reclosing | For supervisor relays: • Verify acceptable measurement of power system input values | Comments: | Test Date: | Verify only the unmonitored relay inputs and outputs that are essential to proper functioning of the Automatic Reclosing | Comments:

## Table 4-2
Table 4-2 Maintenance Activities and Intervals for Automatic Reclosing Components Compontent Type - Control Circuitry Associated with Reclosing and Supervisory Relays (a) - NOT an Integral Part of an RAS; (b) - ARE an Integral Part of an RAS In boxes provided, site document and page number pointing to the evidence of testing. If the test is not applicable, just type N/A
RF Index Number | Generating Station/ Substation | Component Description (e.g., what does it protect?) | Device Identifier (if applicable) | Table 4-2(a) 12 Calendar Years Unmonitored Control circuitry associated with Automatic Reclosing that is not an integral part of an RAS. |  |  | Table 4-2(b) 6 Calendar Years Close coils or actuators of circuit breakers or similar devices that are used in conjunction with Automatic Reclosing as part of an RAS (regardless of any monitoring of the control circuitry). |  |  | Table 4-2(b) 12 Calendar Years Unmonitored close control circuitry associated with Automatic Reclosing used as an integral part of an RAS.
RF Index Number |  |  |  | Test Date: | Verify that Automatic Reclosing, upon initation, does not issue a premature closing command to the close circuitry. | Comments: | Test Date: | Verify that each close coil or actuator is able to operate the circuit breaker or mitigating device | Comments: | Test Date: | Verify all paths of the control circuits associated with Automatic Reclosing that are essential for proper operation of the RAS. | Comments:

## Table 4-3
Table 4-3 Maintenance Activities and Intervals for Automatic Reclosing Components Compontent Type - Voltage Sensing Devices Associated with Supervisory Relays In boxes provided, site document and page number pointing to the evidence of testing.
RF Index Number | Generating Station/ Substation | Component Description (e.g., what does it protect?) | Device Identifier (if applicable) | 12 Calendar Years Any voltage sensing devices not having monitoring attributes of the category below.
RF Index Number |  |  |  | Test Date: | Verify that voltage signal values are provided to the supervisory relays. | Comments:

## Table 5
Table 5 Maintenance Activities and Intervals for Sudden Pressure Relaying Note: In cases where Components of Sudden Pressure Relaying are common to Components listed in Table 1-5, the Components only need to be tested once during a distinct maintenance interval. In boxes provided, site document and page number pointing to the evidence of testing.
RF Index Number | Generating Station/ Substation | Component Description (e.g., what does it protect?) | Device Identifier (if applicable) | 6 Calendar Years Any fault pressure relay |  |  | 6 Calendar Years Electromechanical lockout devices which are directly in a trip path from the fault pressure relay to the interrupting device trip coil (regardless of any monitoring of the control circuitry). |  |  | 12 Calendar Years Unmonitored control circuitry associated with Sudden Pressure Relaying.
RF Index Number |  |  |  | Test Date: | Verify the pressure or flow sensing mechanism is operable. | Comments: | Test Date: | Verify electrical operation of electromechanical lockout devices | Comments: | Test Date: | Verify all paths of the trip circuits inclusive of all auxiliary relays through the trip coil(s) of the circuit breakers or other interrupting devices. | Comments: