## ReadMe
Acceptable Model Working Group (AMWG) Dynamic Model List
Sheet Name: AMWG Dyamic Model List
- List of dynamic models and model types in MMWG dynamic cases
- Each model to be designated as Acceptable, Not Accepted, Under Review and Needs Review by AMWG members for Eastern Interconnection with any relevant model notes
- Accepted: Model is accepteed by AMWG for use in MMWG cases
- Unacceptable: Model is not accepted by AMWG for use in MMWG cases and should be phased out
- Not Recommended: Model can still be used and cannot be phased out at the moment, but another model is preferred for use
- Under Review: Model is under review by AMWG members
- Needs Review: Model needs to be reviewed by AMWG members
Sheet Name: Metrics
- Provides data on AMWG model designatins for Eastern Interconnection dynamic models
Sheet Name: NERC Un-Acceptable Models
- Models identified by NERC as Un-Acceptable from NERC Dynamic Model Notice

## AMWG Dynamic Model List
ERAG AMWG Dynamic Model List
MMWG Approved PSSE Version: 35.6
ModelName | ModelType |  | Model Description | AMWG Designation [Acceptable, Not Recommended, Under Review, Needs Review, Unacceptable] | Model Usage Notes | NERC Un-Acceptable | Legend: Model Types
ABBSVC1 | PSSE Standard Library | Switched Shunt | SVC Model | Acceptable | v34 format, no ID for switched shunt will default to ID of 1 or first listed switched shunt at bus given. |  | PSSE Standard Library | PSSE Standard Library Model
ABBSVC2 | PSSE Standard Library | Switched Shunt | SVC Model | Acceptable | v35 format |  | UDM DLL | External User Model
AC11C | PSSE Standard Library | Excitation |  | Acceptable
AC6A | PSSE Standard Library | Excitation |  | Acceptable | For use in v34+
AC6C | PSSE Standard Library | Excitation |  | Acceptable
AC7B | PSSE Standard Library | Excitation |  | Acceptable
AC7C | PSSE Standard Library | Excitation |  | Acceptable | For use in v35+
AC7CU1 | UDM DLL | Excitation | User defined machine and all other models | Acceptable | v34 model format. Converts to AC7C in V35+
AC8B | PSSE Standard Library | Excitation |  | Acceptable
AC8BBU1 | UDM DLL | Excitation |  | Acceptable
AC8BBU2 | PSSE Standard Library | Excitation |  | Needs Review | Confirm with Siemens if model matches AC8BBU1
AEINX | UDM DLL | Generator | User defined dynamic machine load model | Needs Review | V34 Model, Retired for V35+
BASOELU1 | UDM DLL | Max/Over Excitation Limiter | OEL | Acceptable
BASOELU2 | PSSE Standard Library | Max/Over Excitation Limiter | OEL | Needs Review
BBGOV1 | PSSE Standard Library | Governor |  | Acceptable
BBSEX1 | PSSE Standard Library | Excitation |  | Acceptable
BSTSV3 | UDM DLL | Generator | User defined dynamic machine load model | Acceptable
C_ABB_MTM_230 | UDM DLL | Generator | User defined dynamic machine load model found in ABB dll | Needs Review
CABBO2 | UDM DLL | Generator | User defined dynamic machine load model | Acceptable
CCOMP4A | PSSE Standard Library | Compensator |  | Acceptable | For use in v35+ This model is bugged and cant be read by PSSE if saved out of PSSE, the quotes in ICONs are a problem.
CCOMP4U1 | PSSE Standard Library | Compensator | User defined machine and all other models | Acceptable | v34 model format. CCOMP4A preffered for v35+
CDC1T | PSSE Standard Library | Two Terminal DC |  | Not Recommended | This model is obsoleted, MH has replaced this one with CDC6T in 2024 series.
CDC4SN | UDM DLL | Two Terminal DC | User defined component model found in cdc4sn-rev1.1.obj | Needs Review | V34 model
CDC4T | PSSE Standard Library | Two Terminal DC |  | Acceptable | V35 Model, replacing CDC4SN
CDC6T | PSSE Standard Library | Two Terminal DC |  | Acceptable
CDC7T | PSSE Standard Library | Two Terminal DC |  | Acceptable
CDCABT | PSSE Standard Library | Two Terminal DC |  | Acceptable
CDCMC | UDM DLL | Two Terminal DC | User defined component model found in NYISO dll | Not Recommended | Version issue - needs to be updated for V36
CDCSID | UDM DLL | Two Terminal DC | User defined component model found in NYISO dll | Not Recommended | Version issue - needs to be updated for V36
CDOKL1 | UDM DLL | Two Terminal DC | User defined component model found in ABB dll | Acceptable
CDSMS1 | PSSE Standard Library | Generator |  | Acceptable
CDVAR3 | UDM DLL | Generator | User defined dynamic machine load model | Acceptable
CDVAR4 | UDM DLL | Generator | User defined dynamic machine load model | Acceptable
CDVAR5 | UDM DLL | Generator | User defined machine and all other models | Acceptable
CDVAR7U1 | PSSE Standard Library | FACTS | AMSC D-VAR Model | Acceptable | Documentaiton found in Vendor Specific Models
CELIN | PSSE Standard Library | Excitation |  | Acceptable
CEmpty | UDM DLL | Generator | User defined dynamic machine load model found in ABB dll | Acceptable
CHASVC101 | UDM DLL | Generator | User defined dynamic machine load model found in NYISO dll | Needs Review
CHASVC102 | UDM DLL | Generator | User defined dynamic machine load model found in NYISO dll | Needs Review
CHSVCT | PSSE Standard Library | Switched Shunt |  | Acceptable | v34 format, no ID for switched shunt will default to ID of 1 or first listed switched shunt at bus given.
CHTFWX | UDM DLL | Two Terminal DC | User defined component model found in NYISO dll | Acceptable
CHTRVX | UDM DLL | Two Terminal DC | User defined component model found in NYISO dll | Acceptable
CIMTR3 | PSSE Standard Library | Generator | Induction Generator | Acceptable
CMDS | UDM DLL | Two Terminal DC | User defined component model found in NYISO dll | Acceptable
COMP | PSSE Standard Library | Compensator |  | Acceptable
COMPCC | PSSE Standard Library | Compensator |  | Unacceptable |  | Y
CP20025702 | UDM DLL | Renewable Machine | User defined dynamic machine load model | Needs Review
CP200651001 | UDM DLL | Renewable Machine | User defined dynamic machine load model | Needs Review
CP200660000 | UDM DLL | Renewable Machine | User defined dynamic machine load model found in Vestas dll | Needs Review
CP200660602 | UDM DLL | Renewable Machine | User defined dynamic machine load model found in Vestas dll | Needs Review
CP200661102 | UDM DLL | Renewable Machine | User defined dynamic machine load model found in Vestas dll | Needs Review
CP220960602 | UDM DLL | Renewable Machine | User defined dynamic machine load model found in Vestas dll | Needs Review
CP220961102 | UDM DLL | Renewable Machine | User defined dynamic machine load model found in Vestas dll | Needs Review
CRCMGV | PSSE Standard Library | Governor | Cross Compound Governor | Acceptable
CSSCST | PSSE Standard Library | Switched Shunt | SVC model | Acceptable | v34 format, no ID for switched shunt will default to ID of 1 or first listed switched shunt at bus given.
CSSCST2 | PSSE Standard Library | Switched Shunt | SVC model | Acceptable | v35 format
CSTATT | PSSE Standard Library | Generator | Static Condesor FACTS model | Acceptable
CSVGN1 | PSSE Standard Library | Generator | Static Shunt Compensator | Acceptable
CSVGN3 | PSSE Standard Library | Generator | Static Shunt Compensator | Acceptable
CSVGN4 | PSSE Standard Library | Generator | Static Shunt Compensator | Acceptable
CSVGN5 | PSSE Standard Library | Generator | Static VAR Compensator | Acceptable
DC3A | PSSE Standard Library | Excitation |  | Acceptable
DC4B | PSSE Standard Library | Excitation |  | Acceptable
DC4C | PSSE Standard Library | Excitation |  | Acceptable | For use in v35+
DC4CU1 | PSSE Standard Library | Excitation | User defined machine and all other models | Acceptable | v34 model format. Converts to DC4C for v35+
DCRED1U1 | UDM DLL | MISC | User defined machine switching model found in MHDCcntrlCDC7T_35.obj | Acceptable
DCREDFU1 | UDM DLL | MISC | User defined machine switching model found in MHDCcntrlCDC7T_35.obj | Acceptable
DCREDRU1 | UDM DLL | MISC | User defined machine switching model found in MHDCcntrlCDC7T_35.obj | Acceptable
DEGOV | PSSE Standard Library | Governor |  | Acceptable
DEGOV1 | PSSE Standard Library | Governor |  | Needs Review | Use DEGOV1D which includes deadband
DERA1 | PSSE Standard Library | Renewable Machine | DER Modeled as Machine | Acceptable | For use in v35+
DERAU1 | PSSE Standard Library | Renewable Machine | User defined machine and all other models | Acceptable | v34 model format. Converts to DERA1 for v35+
DISTR1 | PSSE Standard Library | Line Relay | Distance Relay | Acceptable
ESAC1A | PSSE Standard Library | Excitation |  | Acceptable
ESAC2A | PSSE Standard Library | Excitation |  | Acceptable
ESAC3A | PSSE Standard Library | Excitation |  | Acceptable
ESAC4A | PSSE Standard Library | Excitation |  | Acceptable
ESAC5A | PSSE Standard Library | Excitation |  | Acceptable
ESAC6A | PSSE Standard Library | Excitation |  | Needs Review
ESAC8B | PSSE Standard Library | Excitation |  | Acceptable
ESDC1A | PSSE Standard Library | Excitation |  | Acceptable
ESDC2A | PSSE Standard Library | Excitation |  | Acceptable
ESST1A | PSSE Standard Library | Excitation |  | Acceptable
ESST2A | PSSE Standard Library | Excitation |  | Acceptable
ESST3A | PSSE Standard Library | Excitation |  | Acceptable
ESST4B | PSSE Standard Library | Excitation |  | Acceptable
ESURR1 | UDM DLL | Excitation | Found in NYISO dll | Acceptable
EV211460000 | UDM DLL | Renewable Machine | User defined dynamic machine load model found in Vestas dll | Needs Review
EX2000 | PSSE Standard Library | Excitation |  | Unacceptable |  | Y
EX21BR | UDM DLL | Excitation | User defined dynamic machine load model | Needs Review | Not present in 10 year out case, retired?
EXAC1 | PSSE Standard Library | Excitation |  | Acceptable
EXAC1A | PSSE Standard Library | Excitation |  | Acceptable
EXAC2 | PSSE Standard Library | Excitation |  | Acceptable
EXAC3 | PSSE Standard Library | Excitation |  | Acceptable
EXAC4 | PSSE Standard Library | Excitation |  | Acceptable
EXBAS | PSSE Standard Library | Excitation |  | Acceptable
EXDC2 | PSSE Standard Library | Excitation |  | Acceptable
EXF2 | UDM DLL | Generator | User defined dynamic machine load model | Needs Review
EXHQSC | UDM DLL | Excitation | User defined dynamic machine load model found in NYISO dll | Acceptable
EXOEL | UDM DLL | Max/Over Excitation Limiter | User defined dynamic machine load model | Acceptable
EXPIC1 | PSSE Standard Library | Excitation |  | Acceptable
EXSCAZ | UDM DLL | Excitation | User defined dynamic machine load model found in NYISO dll | Acceptable
EXSCEZ | UDM DLL | Excitation | User defined dynamic machine load model found in NYISO dll | Acceptable
EXSCMZ | UDM DLL | Excitation | User defined dynamic machine load model found in NYISO dll | Acceptable
EXST1 | PSSE Standard Library | Excitation |  | Acceptable | SPP Members have provided concerns over the use of this model and "false positives" for transient voltage violations
EXST2 | PSSE Standard Library | Excitation |  | Acceptable
EXST2A | PSSE Standard Library | Excitation |  | Acceptable
EXST3 | PSSE Standard Library | Excitation |  | Acceptable
EXUEL | UDM DLL | Minimum Exciter/Under Exciter | User defined dynamic machine load model | Acceptable
FCVWTU1 | PSSE Standard Library | Renewable Machine | Vestas Model | Needs Review | Documentaiton found in Vendor Specific Models
FLYWLU | UDM DLL | Generator | User defined dynamic machine load model found in FLYWLU_v35.dll | Needs Review | Only found in v35+
FRQDCA | PSSE Standard Library | MISC | Under/Over Frequency Generator Relay disconnects entire Generator Bus | Unacceptable | Must use 8 digit code Machine Bus number plus two digit counter (123456xx). Cannot use 0 for ICONs M and M+1 or model doesn’t work. Converts to FRQDCAT. Unusable in V36
FRQDCAT | PSSE Standard Library | MISC | Under/Over Frequency Generator Relay disconnects entire Generator Bus | Acceptable | Must use 8 digit code Machine Bus number plus two digit counter (123456xx). Cannot use 0 for ICONs M and M+1 or model doesn’t work.
FRQTPA | UDM DLL | MISC | Under/Over Frequency Generator Relay disconnects only Generator | Unacceptable | Must use 8 digit code Machine Bus number plus two digit counter (123456xx). Cannot use 0 for ICONs M and M+1 or model doesn’t work. Unusable in V36
FRQTPAT | PSSE Standard Library | MISC | Under/Over Frequency Generator Relay disconnects only Generator | Acceptable | Must use 8 digit code Machine Bus number plus two digit counter (123456xx). Cannot use 0 for ICONs M and M+1 or model doesn’t work.
GAST | PSSE Standard Library | Governor |  | Unacceptable |  | Y
GAST2A | PSSE Standard Library | Governor |  | Unacceptable |  | Y
GASTWD | PSSE Standard Library | Governor |  | Unacceptable |  | Y
GENCLS | PSSE Standard Library | Generator |  | Unacceptable | Documented Exceptions only | Y
GENQEC | PSSE Standard Library | Generator |  | Acceptable | For use in v36+
GENQECU | PSSE Standard Library | Generator |  | Acceptable | GENQEC preferred for v36+
GENROE | PSSE Standard Library | Generator |  | Not Recommended | Newer Model GENQEC Available - If provides improved response
GENROU | PSSE Standard Library | Generator |  | Not Recommended | Newer Model GENQEC Available - If provides improved response
GENSAE | PSSE Standard Library | Generator |  | Acceptable
GENSAL | PSSE Standard Library | Generator |  | Unacceptable |  | Y
GENTPJ1 | PSSE Standard Library | Generator |  | Not Recommended | For use in v35+ Reccomend using GENQEC. AMWG to develop communication document providing reccomendation and timeline on model phase out. SPP has retired this model
GENTPJU1 | PSSE Standard Library | Generator | User defined machine and all other models | Not Recommended | v34 model format. Reccomend using GENQEC. AMWG to develop communication document providing reccomendation and timeline on model phase out. SPP has retired this model
GEWCS0801 | UDM DLL | Load Control | User defined dynamic machine load model | Needs Review
GEWT2MU1 | PSSE Standard Library | Renewable Mechanical | GE Wind Turbine | Needs Review | Documentaiton found in Vendor Specific Models
GEWTA0705 | UDM DLL | Governor | User defined dynamic machine load model found in GEWTG0705_v35.dll | Acceptable
GEWTA0801 | UDM DLL | Governor | User defined dynamic machine load model | Acceptable
GEWTARU1 | PSSE Standard Library | Renewable Aerodynamic | GE Wind Turbine | Needs Review | Documentaiton found in Vendor Specific Models
GEWTE0705 | UDM DLL | Excitation | User defined dynamic machine load model found in GEWTG0705_v35.dll | Acceptable
GEWTE0801 | UDM DLL | Excitation | User defined dynamic machine load model | Acceptable
GEWTE2 | UDM DLL | Excitation | User defined dynamic machine load model | Unacceptable | V33 model
GEWTECU1 | PSSE Standard Library | Renewable Electrical | GE Wind Turbine | Needs Review | Documentaiton found in Vendor Specific Models
GEWTG0705 | UDM DLL | Generator | User defined dynamic machine load model found in GEWTG0705_v35.dll | Acceptable
GEWTG0801 | UDM DLL | Generator | User defined dynamic machine load model | Acceptable
GEWTG2 | UDM DLL | Generator | User defined dynamic machine load model | Unacceptable | V33 model
GEWTGCU1 | PSSE Standard Library | Renewable Machine | GE Wind Turbine | Needs Review | Documentaiton found in Vendor Specific Models
GEWTGDU1 | PSSE Standard Library | Renewable Gust | GE Wind Turbine | Needs Review | Documentaiton found in Vendor Specific Models
GEWTP2 | UDM DLL | Machine Other | User defined dynamic machine load model | Unacceptable | V33 model
GEWTPTU1 | PSSE Standard Library | Renewable Pitch | GE Wind Turbine | Needs Review | Documentaiton found in Vendor Specific Models
GEWTT1 | UDM DLL | Governor | User defined dynamic machine load model | Unacceptable | V33 model
GFT8WN | UDM DLL | Governor | User defined dynamic machine load model found in NYISO dll | Not Recommended | Issues initializing
GGOV1 | PSSE Standard Library | Governor |  | Acceptable
GGOV1D | PSSE Standard Library | Governor |  | Acceptable | For use in v35+
GGOV1DU | PSSE Standard Library | Governor | User defined machine and all other models | Acceptable | v34 model format. Converts to GGOV1D for v35+
GSCOR2 | UDM DLL | Renewable Machine | User defined dynamic machine load model | Unacceptable | For use in v34 (and earlier versions)
GSLVR2 | UDM DLL | Renewable Mechanical | User defined dynamic machine load model | Unacceptable | For use in v34 (and earlier versions)
GSPWR2 | UDM DLL | Renewable Pitch | User defined dynamic machine load model | Unacceptable | For use in v34 (and earlier versions)
GSVAR2 | UDM DLL | Renewable Electrical | User defined dynamic machine load model | Unacceptable | For use in v34 (and earlier versions)
GSVPR2 | UDM DLL | Renewable Aerodynamic | User defined dynamic machine load model | Unacceptable | For use in v34 (and earlier versions)
GXX043 | UDM DLL | Generator | User defined dynamic machine load model | Unacceptable
H6E1 | PSSE Standard Library | Governor |  | Acceptable | For use in v35+
H6EU1 | PSSE Standard Library | Governor | User defined machine and all other models | Acceptable | v34 model format. Converts to H6E1 for v35+
HQRVC | UDM DLL | Governor | User defined dynamic machine load model found in NYISO dll | Needs Review
HQRVM | UDM DLL | Governor | User defined dynamic machine load model found in NYISO dll | Needs Review
HQRVN | UDM DLL | Governor | User defined dynamic machine load model found in NYISO dll | Needs Review
HQRVW | UDM DLL | Governor | User defined dynamic machine load model found in NYISO dll | Needs Review
HYG3 | PSSE Standard Library | Governor |  | Acceptable | For use in v35+
HYG3U1 | PSSE Standard Library | Governor | User defined machine and all other models | Acceptable | v34 model format. Converts to HYG3 for v35+
HYGOV | PSSE Standard Library | Governor |  | Acceptable
HYGOV2 | PSSE Standard Library | Governor |  | Not Recommended
HYGOV4 | UDM DLL | Governor | User defined dynamic machine load model found in NYISO dll | Needs Review
HYGOVR1 | PSSE Standard Library | Governor |  | Acceptable
IEE2ST | PSSE Standard Library | Stabilizer | PSS - Power System Stabilizer | Acceptable
IEEEG1 | PSSE Standard Library | Governor |  | Needs Review | Use IEEEG1D which includes deadband
IEEEG1D | PSSE Standard Library | Governor |  | Acceptable | For use in v35+
IEEEG1SDU | PSSE Standard Library | Governor | User defined machine and all other models | Acceptable | v34 model format. Converts to IEEEG1D for v35+
IEEEG2 | PSSE Standard Library | Governor |  | Unacceptable | The AMWG is reviewing this model and will coordinate with NERC going forward. | Y
IEEEG3 | PSSE Standard Library | Governor |  | Acceptable
IEEEST | PSSE Standard Library | Stabilizer | PSS - Power System Stabilizer | Acceptable
IEEET1 | PSSE Standard Library | Excitation |  | Acceptable
IEEET2 | PSSE Standard Library | Excitation |  | Acceptable
IEEET3 | PSSE Standard Library | Excitation |  | Acceptable
IEEET4 | PSSE Standard Library | Excitation |  | Acceptable
IEEET5 | PSSE Standard Library | Excitation |  | Acceptable
IEEEVC | PSSE Standard Library | Compensator |  | Acceptable
IEEEX1 | PSSE Standard Library | Excitation |  | Acceptable
IEEEX2 | PSSE Standard Library | Excitation |  | Acceptable
IEEEX4 | PSSE Standard Library | Excitation |  | Acceptable
IEESGO | PSSE Standard Library | Governor |  | Needs Review | Use IEESGOD which includes deadband
IEEX2A | PSSE Standard Library | Excitation |  | Acceptable
IRRADU1 | PSSE Standard Library | Renewable Pitch | User defined machine and all other models | Acceptable
IVOEX | PSSE Standard Library | Excitation |  | Acceptable
LCFB1 | PSSE Standard Library | Load Control |  | Acceptable
LOEXR1T | PSSE Standard Library | Machine Protection | Loss of Excitation distance Relay | Acceptable
MAXEX1 | PSSE Standard Library | Max/Over Excitation Limiter | OEL | Acceptable
MAXEX2 | PSSE Standard Library | Max/Over Excitation Limiter | OEL | Acceptable
MBPS4S | UDM DLL | Stabilizer | User defined dynamic machine load model found in NYISO dll | Acceptable
MNLEX2 | PSSE Standard Library | Minimum Exciter/Under Exciter |  | Acceptable
MNLEX3 | PSSE Standard Library | Minimum Exciter/Under Exciter |  | Acceptable
NR3AUX | UDM DLL | Two Terminal DC | User defined auxiliary model found in NYISO dll | Acceptable
OEL2C | PSSE Standard Library | Max/Over Excitation Limiter | OEL | Acceptable | For use in v35+
OEL2CU1 | PSSE Standard Library | Max/Over Excitation Limiter | OEL | Acceptable | v34 model format. Converts to OEL2C for v35+
OELHQ | UDM DLL | Max/Over Excitation Limiter | User defined dynamic machine load model found in NYISO dll | Needs Review
ORRCP5 | UDM DLL | MISC | User defined machine switching model | Acceptable
PANELU1 | PSSE Standard Library | Renewable Mechanical | User defined machine and all other models | Acceptable
PAUX12MU1 | UDM DLL | Two Terminal DC | User defined auxiliary model found in NYISO dll | Acceptable
PE_ELC | UDM DLL | Renewable Electrical | User defined dynamic machine load model | Acceptable
PE_PPC | UDM DLL | Renewable Mechanical | User defined dynamic machine load model | Acceptable
PIDGOV | PSSE Standard Library | Governor |  | Needs Review | Use PIDGOVD which includes deadband
PLNTBU1 | PSSE Standard Library | Bus Other | Renewable Plant Controller Model | Acceptable | Paired with REAX3B, REAX4B, SVCAXB, FCTAXB, SYNAXB models
PPCAPW550V51001 | UDM DLL | Renewable Gust | User defined dynamic machine load model | Not Recommended | Versioning Issue - does not work for V35 and on
PPCAPWM3V4901 | UDM DLL | Renewable Gust | User defined dynamic machine load model | Not Recommended | Versioning Issue - does not work for V35 and on
PPCORE550V51001 | UDM DLL | Renewable Pitch | User defined dynamic machine load model | Not Recommended | Versioning Issue - does not work for V35 and on
PPCOREM3V4901 | UDM DLL | Renewable Pitch | User defined dynamic machine load model | Not Recommended | Versioning Issue - does not work for V35 and on
PPCPMM550V51001 | UDM DLL | Renewable Aerodynamic | User defined dynamic machine load model | Not Recommended | Versioning Issue - does not work for V35 and on
PPCPMMM3V4901 | UDM DLL | Renewable Aerodynamic | User defined dynamic machine load model | Not Recommended | Versioning Issue - does not work for V35 and on
PPCRPW550V51001 | UDM DLL | Renewable Plant Controller | User defined dynamic machine load model | Not Recommended | Versioning Issue - does not work for V35 and on
PPCRPWM3V4901 | UDM DLL | Renewable Plant Controller | User defined dynamic machine load model | Not Recommended | Versioning Issue - does not work for V35 and on
PSS2A | PSSE Standard Library | Stabilizer | PSS - Power System Stabilizer | Acceptable
PSS2B | PSSE Standard Library | Stabilizer | PSS - Power System Stabilizer | Acceptable
PSS2C | PSSE Standard Library | Stabilizer | PSS - Power System Stabilizer | Acceptable | For use in v35+
PSS2CU1 | PSSE Standard Library | Stabilizer | PSS - Power System Stabilizer | Acceptable | v34 model format. Converts to PSS2C for v35+
PVEU1 | PSSE Standard Library | Renewable Electrical |  | Acceptable
PVGU1 | PSSE Standard Library | Renewable Machine |  | Acceptable
PWTBD1 | PSSE Standard Library | Governor |  | Acceptable
REAX3BU1 | PSSE Standard Library | Renewable Plant Controller |  | Acceptable | Type 3 wind turbines plant controller paired with PLNTB model
REAX4BU1 | PSSE Standard Library | Renewable Plant Controller |  | Acceptable | Type 4, Full converter plant controller paired with PLNTB model
REECA1 | PSSE Standard Library | Renewable Electrical |  | Acceptable | For use in v35+
REECAU1 | PSSE Standard Library | Renewable Electrical |  | Acceptable | v34 model format. Converts to REECA1 for v35+
REECB1 | PSSE Standard Library | Renewable Electrical |  | Unacceptable | For use in v35+ | Y
REECBU1 | PSSE Standard Library | Renewable Electrical |  | Unacceptable | v34 model format. Converts to REECB1 for v35+ | Y
REECC1 | PSSE Standard Library | Renewable Electrical |  | Acceptable | For use in v35+
REECCU1 | PSSE Standard Library | Renewable Electrical | User defined machine and all other models | Acceptable | v34 model format. Converts to REECC1 for v35+
REECDU1 | PSSE Standard Library | Renewable Electrical |  | Acceptable
REGCA1 | PSSE Standard Library | Renewable Machine |  | Acceptable | For use in v35+
REGCAU1 | PSSE Standard Library | Renewable Machine |  | Acceptable | v34 model format. Converts to REGCA1 for v35+
REGCAU2 | PSSE Standard Library | Renewable Machine |  | Acceptable
REGCBU1 | PSSE Standard Library | Renewable Machine |  | Acceptable
RELOFU1 | UDM DLL | MISC | User defined machine switching model found in MHDCcntrlCDC7T_35.obj | Acceptable
RELOUF | UDM DLL | CONET |  | Unacceptable
RELOVS | UDM DLL | CONEC |  | Unacceptable
RELUFU1 | UDM DLL | MISC | User defined machine switching model found in MHDCcntrlCDC7T_35.obj | Acceptable
RELUNS | UDM DLL | CONEC |  | Unacceptable
REMCMP | PSSE Standard Library | Compensator |  | Acceptable
REPCA1 | PSSE Standard Library | Renewable Plant Controller |  | Acceptable | For use in v35+
REPCAU1 | PSSE Standard Library | Renewable Plant Controller | User defined machine and all other models | Acceptable | v34 model format. Converts to REPCA1 for v35+
REPCTA1 | PSSE Standard Library | Renewable Plant Controller |  | Acceptable | For use in v35+
REPCTAU1 | PSSE Standard Library | Renewable Plant Controller | User defined machine and all other models | Acceptable | v34 model format. Converts to REPCTA1 for v35+
REXSY1 | PSSE Standard Library | Excitation |  | Acceptable
REXSYS | PSSE Standard Library | Excitation |  | Acceptable
RSPDC3 | UDM DLL | Two Terminal DC | User defined component model found in NYISO dll | Acceptable
S_PFFC | UDM DLL | Generator | User defined dynamic machine load model | Needs Review
SCRX | PSSE Standard Library | Excitation |  | Acceptable
SEXS | PSSE Standard Library | Excitation |  | Unacceptable | Documented Exceptions only | Y
SGT8HM1 | PSSE Standard Library | Governor |  | Acceptable
SITGT1 | PSSE Standard Library | Governor |  | Acceptable | For use in v35+
SITGTU1 | PSSE Standard Library | Governor | User defined machine and all other models | Acceptable | v34 model format. Converts to SITGT1 for v35+
SLNOS1 | PSSE Standard Library | Line Relay | Out of Step Relay | Acceptable
SMASC_ES | UDM DLL | Generator | User defined dynamic machine load model | Needs Review
SMASTP18 | UDM DLL | Generator | User defined dynamic machine load model | Needs Review | DLL File Name
SOLAGT | UDM DLL | Governor | User defined dynamic machine load model | Needs Review
SQBAUT | PSSE Standard Library | Two Terminal DC | Two-Terminal DC Aux Signal | Acceptable
ST1C | PSSE Standard Library | Excitation |  | Acceptable
ST4C | PSSE Standard Library | Excitation |  | Acceptable | For use in v35+
ST4CU1 | PSSE Standard Library | Excitation | User defined machine and all other models | Acceptable | v34 model format. Converts to ST4C for v35+
ST5B | PSSE Standard Library | Excitation |  | Acceptable
ST6B | PSSE Standard Library | Excitation |  | Acceptable
ST6C | PSSE Standard Library | Excitation |  | Acceptable
ST8C | PSSE Standard Library | Excitation |  | Acceptable | For use in v35+
ST8CU1 | PSSE Standard Library | Excitation | User defined machine and all other models | Acceptable | v34 model format. Converts to ST8C for v35+
ST9C | PSSE Standard Library | Excitation |  | Acceptable | For use in v35+
ST9CU1 | PSSE Standard Library | Excitation | User defined machine and all other models | Acceptable | v34 model format. Converts to ST9C for v35+
STAB1 | PSSE Standard Library | Stabilizer | PSS - Power System Stabilizer | Acceptable
STAB4 | PSSE Standard Library | Stabilizer | PSS - Power System Stabilizer | Acceptable
STBSVC | PSSE Standard Library | Stabilizer | PSS - Power System Stabilizer | Acceptable
SUVCXU1 | UDM DLL | Bus Other | User defined bus model found in MHDCcntrlCDC7T_35.obj | Acceptable
SVSMO1T2 | PSSE Standard Library | Switched Shunt | Continuous Control SVC model | Acceptable | For use in v35+
SVSMO1T3 | PSSE Standard Library | Switched Shunt | Continuous Control SVC model | Acceptable | For use in v35+
SVSMO1U1 | PSSE Standard Library | Switched Shunt | Continuous Control SVC model | Acceptable | v34 model format. SVSMO1T2 or SVSMO1T3 preferred for v35+
SVSMO1U2 | PSSE Standard Library | Switched Shunt | Continuous Control SVC model | Acceptable | v34 model format. SVSMO1T2 or SVSMO1T3 preferred for v35+
SVSMO2T2 | PSSE Standard Library | Switched Shunt | Discrete Control SVC model | Acceptable | For use in v35+
SVSMO2T3 | PSSE Standard Library | Switched Shunt | Discrete Control SVC model | Acceptable | For use in v35+
SVSMO2U2 | PSSE Standard Library | Switched Shunt | Discrete Control SVC model | Acceptable | v34 model format. SVSMO2T2 or SVSMO2T3 preferred for v35+
SVSMO3T2 | PSSE Standard Library | FACTS |  | Acceptable | For use in v35+
SVSMO3U2 | PSSE Standard Library | FACTS | User defined FACTS models | Acceptable | v34 model format. Converts to SVSMO3T2 for v35+
SWCAPT | PSSE Standard Library | MISC |  | Acceptable
SWSHNT | PSSE Standard Library | Switched Shunt | Switched Shunt Model | Acceptable | v34 format, no ID for switched shunt will default to ID of 1 or first listed switched shunt at bus given.
SWSHNT2 | PSSE Standard Library | Switched Shunt | Switched Shunt Model | Acceptable | v35 format
TGOV1 | PSSE Standard Library | Governor |  | Needs Review | Use TGOV1D model which includes deadband
TGOV1D | PSSE Standard Library | Governor |  | Acceptable | For use in v35+
TGOV1DU | PSSE Standard Library | Governor | User defined machine and all other models | Acceptable | v34 model format. Converts to TGOV1D for v35+
TGOV2 | PSSE Standard Library | Governor |  | Acceptable
TGOV3 | PSSE Standard Library | Governor |  | Needs Review | Use TGOV3D model which includes deadband
TURCZT | PSSE Standard Library | Governor |  | Acceptable
UDHOLDU1 | UDM DLL | MISC | User defined machine switching model found in NYISO dll | Acceptable
UEL2 | PSSE Standard Library | Minimum Exciter/Under Exciter |  | Acceptable
UEL2C | PSSE Standard Library | Minimum Exciter/Under Exciter |  | Acceptable | For use in v35+
UEL2CU1 | PSSE Standard Library | Minimum Exciter/Under Exciter | User defined machine and all other models | Acceptable | v34 model format. Converts to UEL2C for v35+
URGS3T | PSSE Standard Library | Governor |  | Unacceptable |  | Y
URRTGT | UDM DLL | Governor | User defined dynamic machine load model | Needs Review
USAC6AU | UDM DLL | Excitation | User defined machine and all other models | Acceptable | v33 model format. Converts to AC6A for v34+
UST8HM | UDM DLL | Governor | User defined dynamic machine load model | Needs Review | Made into Standard Library Model. SGT8HM1.
UST8HS | UDM DLL | Governor | User defined dynamic machine load model | Needs Review | Made into Standard Library Model. SGT8HS1.
VC19024901 | UDM DLL | Renewable Machine | User defined dynamic machine load model | Needs Review
VC200460602 | UDM DLL | Renewable Machine | User defined dynamic machine load model found in Vestas dll | Needs Review
VFT1 | PSSE Standard Library | Two-winding Transformer |  | Acceptable
VIECPCU1 | PSSE Standard Library | Renewable Plant Controller | Vestas Model | Needs Review | Documentaiton found in Vendor Specific Models
VIECPCU2 | PSSE Standard Library | Renewable Plant Controller | Vestas Model | Needs Review | Documentaiton found in Vendor Specific Models
VPERHZ1 | PSSE Standard Library | Machine Protection | Voltage Per Hertz | Acceptable | For use in v35+ (This is bugged and cant be read by PSSE v35. Use v34 format)
VPERHZU1 | PSSE Standard Library | Machine Protection | Voltage Per Hertz | Acceptable | v34 model format. Converts to VPERHZ1 for v35+
VPPC20300V61102 | UDM DLL | Renewable Pitch | User defined dynamic machine load model found in Vestas dll | Not Recommended | V34 Model
VPPC50400V60602 | UDM DLL | Renewable Pitch | User defined dynamic machine load model found in Vestas dll | Not Recommended | `
VPPC50800V60602 | UDM DLL | Renewable Pitch | User defined dynamic machine load model found in Vestas dll | Not Recommended | V34 Model
VPPC51100V61102 | UDM DLL | Renewable Pitch | User defined dynamic machine load model found in Vestas dll | Needs Review | Plant Controller
VS17074901 | UDM DLL | Renewable Machine | User defined dynamic machine load model | Needs Review
VS200461102 | UDM DLL | Renewable Machine | User defined dynamic machine load model found in Vestas dll | Acceptable | Specific dispatch required
VSCDCT | PSSE Standard Library | VSC DC |  | Acceptable
VTGDCA | PSSE Standard Library | MISC | Under/Over Voltage Generator Relay disconnects Entire Generator Bus | Acceptable | Must use 8 digit code Machine Bus number plus two digit counter (123456xx). Cannot use 0 for ICONs M and M+1 or model doesn’t work. Converts to VTGDCAT.
VTGDCAT | PSSE Standard Library | MISC | Under/Over Voltage Generator Relay disconnects Entire Generator Bus | Acceptable | Must use 8 digit code Machine Bus number plus two digit counter (123456xx). Cannot use 0 for ICONs M and M+1 or model doesn’t work.
VTGTPA | UDM DLL | MISC | Under/Over Voltage Generator Relay disconnects Generator Only | Acceptable | Must use 8 digit code Machine Bus number plus two digit counter (123456xx). Cannot use 0 for ICONs M and M+1 or model doesn’t work.
VTGTPAT | PSSE Standard Library | MISC | Under/Over Voltage Generator Relay disconnects Generator Only | Acceptable | Must use 8 digit code Machine Bus number plus two digit counter (123456xx). Cannot use 0 for ICONs M and M+1 or model doesn’t work.
VWPOS7 | UDM DLL | Renewable Gust | User defined dynamic machine load model | Needs Review | V34 Model
VWRES7 | UDM DLL | Renewable Plant Controller | User defined dynamic machine load model | Needs Review | V34 Model
W4E2U | UDM DLL | Renewable Electrical | User defined dynamic machine load model | Unacceptable | Converted to WT4E2; converted model is unacceptable.
W4G2U | UDM DLL | Renewable Machine | User defined dynamic machine load model | Unacceptable | Converted to WT4G2; converted model is unacceptable.
WEHGOV | PSSE Standard Library | Governor |  | Acceptable
WELDCC | UDM DLL | Two Terminal DC | User defined component model found in WELDCC_35.dll | Acceptable
WESGOV | PSSE Standard Library | Governor |  | Unacceptable | The AMWG is reviewing this model and will coordinate with NERC going forward. | Y
WPIDHY | PSSE Standard Library | Governor |  | Needs Review | Use WPIDHYD model which includes deadband
WSHYDD | PSSE Standard Library | Governor |  | Acceptable
WSHYGP | PSSE Standard Library | Governor |  | Acceptable
WSIEG1 | PSSE Standard Library | Governor |  | Acceptable
WT12A1 | PSSE Standard Library | Renewable Aerodynamic |  | Unacceptable |  | Y
WT12A1U_B | UDM DLL | Renewable Aerodynamic | User defined dynamic machine load model | Acceptable
WT12T1 | PSSE Standard Library | Renewable Mechanical |  | Acceptable
WT1G1 | PSSE Standard Library | Renewable Machine |  | Acceptable
WT2E1 | PSSE Standard Library | Renewable Electrical |  | Acceptable
WT2G1 | PSSE Standard Library | Renewable Machine |  | Acceptable
WT3E1 | PSSE Standard Library | Renewable Electrical |  | Unacceptable |  | Y
WT3G1 | PSSE Standard Library | Renewable Machine |  | Unacceptable |  | Y
WT3G2 | PSSE Standard Library | Renewable Machine |  | Unacceptable |  | Y
WT3P1 | PSSE Standard Library | Renewable Pitch |  | Unacceptable |  | Y
WT3T1 | PSSE Standard Library | Renewable Mechanical |  | Unacceptable |  | Y
WT4E1 | PSSE Standard Library | Renewable Electrical |  | Unacceptable |  | Y
WT4E2 | PSSE Standard Library | Renewable Electrical |  | Unacceptable |  | Y
WT4G1 | PSSE Standard Library | Renewable Machine |  | Unacceptable |  | Y
WT4G2 | PSSE Standard Library | Renewable Machine |  | Unacceptable |  | Y
WTARA1 | PSSE Standard Library | Renewable Aerodynamic |  | Acceptable | For use in v35+
WTARAU1 | PSSE Standard Library | Renewable Aerodynamic | User defined machine and all other models | Acceptable | v34 model format. Converts to WTARA1 for v35+
WTDTA1 | PSSE Standard Library | Renewable Mechanical |  | Acceptable | For use in v35+
WTDTAU1 | PSSE Standard Library | Renewable Mechanical | User defined machine and all other models | Acceptable | v34 model format. Converts to WTDTA1 for v35+
WTPTA1 | PSSE Standard Library | Renewable Pitch |  | Acceptable | For use in v35+
WTPTAU1 | PSSE Standard Library | Renewable Pitch | User defined machine and all other models | Acceptable | v34 model format. Converts to WTPTA1 for v35+
WTTQA1 | PSSE Standard Library | Torque Controller |  | Acceptable
WTTQAU1 | PSSE Standard Library | Torque Controller | User defined machine and all other models | Acceptable | v34 model format. Converts to WTPTA1 for v35+
SIECU1 | UDM DLL | Bus Other | User Defined model to work with standard library model and Vestas UDM | Acceptable | Plant Controller for wind farm in Michigan.
OEL5CU1 | PSSE Standard Library | Max/Over Excitation Limiter | OEL | Acceptable
AC1C | PSSE Standard Library | Excitation |  | Acceptable
CP212261107 | UDM DLL | Renewable Machine | User defined dynamic machine model found in Vestas dll | Acceptable
CP232671500 | UDM DLL | Renewable Machine | User defined dynamic machine model found in Vestas dll | Acceptable
CP211460000 | UDM DLL | Renewable Machine | User defined dynamic machine model found in Vestas dll | Acceptable
VPPC50600V61107 | UDM DLL | Renewable Pitch | User defined dynamic machine model found in Vestas dll | Acceptable | Plant Controller
VPPC51200V71500 | UDM DLL | Renewable Pitch | User defined dynamic machine model found in Vestas dll | Acceptable | Plant Controller
VPPC50800V60000 | UDM DLL | Renewable Pitch | User defined dynamic machine model found in Vestas dll | Acceptable | Plant Controller
CSWSHNVWSV101 | UDM DLL | Switched Shunt | User defined switched shunt model found in Vestas dll | Acceptable

## Metrics
ERAG AMWG Dynamic Model Metrics
Model Type | Model Count | AMWG Acceptable | AMWG Not Recommended | AMWG Unacceptable | AMWG Under Review | AMWG Needs Review | Count of NERC Un-Acceptable
PSSE Standard Library | 240 | 191 | 6 | 24 | 0 | 19 | 23
UDM DLL | 119 | 53 | 14 | 16 | 0 | 36 | 0
Model Totals | 359 | 244 | 20 | 40 | 0 | 55 | 23

## NERC Un-Acceptable Models
ModelName | Model Description | NERC Dynamic Model Notice (July 2023)
WT3G1 | Generic Type 3 WTG Generator/Converter Model - Doubly-fed inductiongenerator
WT3G2 | Generic Type 3 WTG Generator/Converter Model - Doubly-fed inductiongenerator
wt3g | Generic Type 3 WTG Generator/Converter Model - Doubly-fed inductiongenerator
WT4G1 | Generic Type 4 WTG Generator/Converter Model - Variable speed generator withfull converter
WT4G2 | Generic Type 4 WTG Generator/Converter Model - Variable speed generator withfull converter
wt4g | Generic Type 4 WTG Generator/Converter Model - Variable speed generator withfull converter
WT3E1 | Generic Type 3 WTG Electrical Control Model
wt3e | Generic Type 3 WTG Electrical Control Model
WT4E1 | Generic Type 4 WTG Electrical Control Model
WT4E2 | Generic Type 4 WTG Electrical Control Model
wt4e | Generic Type 4 WTG Electrical Control Model
WT3T1 | Generic Type 3 WTG Turbine Model
wt3t | Generic Type 3 WTG Turbine Model
WT3P1 | Generic Type 3 WTG Pitch Control Model
wt3p | Generic Type 3 WTG Pitch Control Model
WT12A1 | Generic Type 1 and 2 WTG Pitch Control Model
wt1p | Generic Type 1 and 2 WTG Pitch Control Model
wt2p | Generic Type 1 and 2 WTG Pitch Control Model
WT4E1 | Generic Type 4 WTG Power Converter Model
wt4t | Generic Type 4 WTG Power Converter Model
wt4p | Generic Type 4 Pitch Control Model
REECB1 | Generic Phase 2 PV Electrical Controls Model
REECBU1 | Generic Phase 2 PV Electrical Controls Model
reec_b | Generic Phase 2 PV Electrical Controls Model
genwri | Vestas Model of Wound-Rotor Induction Generator (with Variable External RotorResistance)
exwtg1 | Vestas Model of Rotor Resistance Control for Wound-Rotor Induction WTG
wndtge | GE Wind Turbine Control Model - Doubly Fed Induction Generator (DFIG) and Full Converter (FC) Models
gewtg | GE Wind Turbine Generator/Converter - DFAG and FC Models
exwtge | GE Wind Turbine Excitation (converter) Control Model for DFAG Generators
wndvar | GE Wind Turbine Plant-Level Supervisory Voltage/VAR Control
GENSAL | Salient Pole Generator Model (IEEE Std 1110 §5.3.1 Model 2.1)
gensal | Salient Pole Generator Model (IEEE Std 1110 §5.3.1 Model 2.1)
GENCLS | Classical Generator Model (IEEE Std 1110 §5.4.2)
gencls | Classical Generator Model (IEEE Std 1110 §5.4.2)
GENTRA | Transient Level Generator Model
texs | General Purpose Transformer Fed Excitation System
SEXS | Simplified Excitation System
sexs | Simplified Excitation System
EX2000 | GE EX2000 Excitation System
COMPCC | Cross and Joint Current Compensation Model
ccomp | Cross and Joint Current Compensation Model
lm2500 | LM 2500 Aero-Derivative Gas Turbine Governor Model
lm6000 | LM 6000 Aero-Derivative Gas Turbine Governor Model
URGS3T | WECC Gas Turbine Governor Model
gast | WECC Gas Turbine Governor Model
GAST | Gas Turbine-Governor Model
GAST2A | Gas Turbine-Governor Model
GASTWD | Gas turbine-governor
IEEEG2 | 1981 IEEE Type 2 General Approx. Linear Ideal Hydro Model
WESGOV | Westinghouse Digital Governor Model for Gas Turbines
motorc | Phasor Model of Single-Phase Air-Conditioner Compressor Motor
mslr1 | Mechanically Switched Line Reactor

## Version
Version | Approval Date
Version 1 | 2025-07-15