## Requirements-Higher Likelihood
Standard | Requirement | Requirement Text | Potentially Impacted by Generator Uprate? | Analysis
FAC-002-4 | R2. | Each Generator Owner seeking to interconnect new generation Facilities, or existing interconnections of generation Facilities seeking to make a qualified change as defined by the Planning Coordinator under Requirement R6, shall coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | Possible | Entity should review its planned uprate changes against the Planning Coordinator's definition of "qualified change" to determine if it will trigger study coordination efforts. | ReliabilityFirst disclaims any use of this sheet as being the complete universe of potentially implicated standards for all generator uprates or configuration changes. It is intended as a useful tool in starting your compliance analysis, when considering a generator uprate.
FAC-002-4 | R5. | Each applicable Generator Owner shall coordinate and cooperate with its Transmission Planner or Planning Coordinator on studies regarding requested interconnections to its Facilities, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | Possible | Entity should review its planned uprate changes against the Planning Coordinator's definition of "qualified change" to determine if it will trigger study coordination efforts.
FAC-008-5 | R1. | R1. Each Generator Owner shall have documentation for determining the Facility Ratings of its solely and jointly owned generator Facility(ies) up to the low side terminals of the main step up transformer if the Generator Owner does not own the main step up transformer and the high side terminals of the main step up transformer if the Generator Owner owns the main step up transformer. [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] 1.1. The documentation shall contain assumptions used to rate the generator and at least one of the following: • Design or construction information such as design criteria, ratings provided by equipment manufacturers, equipment drawings and/or specifications, engineering analyses, method(s) consistent with industry standards (e.g. ANSI and IEEE), or an established engineering practice that has been verified by testing or engineering analysis. • Operational information such as commissioning test results, performance testing or historical performance records, any of which may be supplemented by engineering analyses. 1.2. The documentation shall be consistent with the principle that the Facility Ratings do not exceed the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. | Possible | Entity should review its planned uprate changes against its R1 documentation for determining Facility Ratings and revise or adjust as necessary.
FAC-008-5 | R2. | R2. Each Generator Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned equipment connected between the location specified in R1 and the point of interconnection with the Transmission Owner that contains all of the following. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] 2.1. The methodology used to establish the Ratings of the equipment that comprises the Facility(ies) shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronic Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. 2.2. The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R2, Part 2.1 including identification of how each of the following were considered: 2.2.1. Equipment Rating standard(s) used in development of this methodology. 2.2.2. Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. 2.2.3. Ambient conditions (for particular or average conditions or as they vary in real-time). 2.2.4. Operating limitations.1 2.3. A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. 2.4. The process by which the Rating of equipment that comprises a Facility is determined. 2.4.1. The scope of equipment addressed shall include, but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. 2.4.2. The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. | Possible | Entity should review its planned uprate changes against its R2 documentation for determining Facility Ratings and revise or adjust as necessary.
FAC-008-5 | R6. | R6. Each Transmission Owner and Generator Owner shall have Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings methodology or documentation for determining its Facility Ratings. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | Possible | Entity should review its planned uprate changes against its Facility Ratings methodology, and develop its Facility Ratings accordingly.
FAC-008-5 | R8. | R8. Each Transmission Owner (and each Generator Owner subject to Requirement R2) shall provide requested information as specified below (for its solely and jointly owned Facilities that are existing Facilities, new Facilities, modifications to existing Facilities and re-ratings of existing Facilities) to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s): [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] 8.1. As scheduled by the requesting entities: 8.1.1. Facility Ratings 8.1.2. Identity of the most limiting equipment of the Facilities 8.2. Within 30 calendar days (or a later date if specified by the requester), for any requested Facility with a Thermal Rating that limits the use of Facilities under the requester’s authority by causing any of the following: 1) An Interconnection Reliability Operating Limit, 2) A limitation of Total Transfer Capability, 3) An impediment to generator deliverability, or 4) An impediment to service to a major load center: 8.2.1. Identity of the existing next most limiting equipment of the Facility 8.2.2. The Thermal Rating for the next most limiting equipment identified in Requirement R8, Part 8.2.1. | Possible | Entity should communicate the requested information to its RC, PC, TP, TO, and TOP, following modifying its Facilities.
MOD-025-2 | R1. | Each Generator Owner shall provide its Transmission Planner with verification of the Real Power capability of its applicable Facilities as follows: 1.1. Verify the Real Power capability of its generating units in accordance with Attachment 1. 1.2. Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. | Possible | Entity should review Attachment 1 to MOD-025-2 to determine if the uprate triggers capability verification.
MOD-025-2 | R2. | Each Generator Owner shall provide its Transmission Planner with verification of the Reactive Power capability of its applicable Facilities as follows: 2.1. Verify, in accordance with Attachment 1, (i) the Reactive Power capability of its generating units and (ii) the Reactive Power capability of its synchronous condenser units. 2.2. Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. | Possible | Entity should review Attachment 1 to MOD-025-2 to determine if the uprate triggers capability verification.
MOD-026-2 | R4. | Each Generator Owner or Transmission Owner shall, within 180 calendar days after making a hardware, software, firmware, control mode, or setting change(s)8 to an applicable unit or facility that alters the dynamic response characteristic(s), provide its Transmission Planner with updated model(s) and accompanying documentation as described in Requirement R2, Parts 2.1 through 2.3 and, if applicable, Requirement R3, Parts 3.1 through 3.5. If mutually agreed upon with the Transmission Planner, model(s) and accompanying documentation may be provided according to a revised timeline. | Possible | Entity should determine if the planned uprate involves a hardware, software, firmware, control mode, or settings change that alters dynamic response characteristics.
MOD-032-1 | R2. | Each Balancing Authority, Generator Owner, Load Serving Entity, Resource Planner, Transmission Owner, and Transmission Service Provider shall provide steady-state, dynamics, and short circuit modeling data to its Transmission Planner(s) and Planning Coordinator(s) according to the data requirements and reporting procedures developed by its Planning Coordinator and Transmission Planner in Requirement R1. For data that has not changed since the last submission, a written confirmation that the data has not changed is sufficient. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | Possible | Review the TP and PCs data requirements and reporting procedures in R1 to determine what data must be reported associated with the uprate.
PRC-002-5 | R2. | R2. Each Transmission Owner and Generator Owner shall have SER data for circuit breaker position (open/close) for each circuit breaker it owns directly connected to the BES buses identified in Requirement R1 and associated with the BES Elements at those BES buses. [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | Possible | An uprate is unlikely to directly impact PRC-002 requirements, however the plant should verify that SER capabilities are restored once generator has returned to service following completion of uprate project work.
PRC-002-5 | R3. | R3. Each Transmission Owner and Generator Owner shall have FR data to determine the following electrical quantities for each triggered FR for the BES Elements it owns directly connected to the BES buses identified in Requirement R1: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] 3.1. Phase-to-neutral voltage for each phase of each specified BES bus. 3.2. Each phase current and the residual or neutral current for the following BES Elements: 3.2.1. Transformers that have a low-side operating voltage of 100 kV or above. 3.2.2. Transmission Lines. | Possible | An uprate is unlikely to directly impact PRC-002 requirements, however the plant should verify that FR capabilities are restored once generator has returned to service following completion of uprate project work.
PRC-002-5 | R4. | R4. Each Transmission Owner and Generator Owner shall have FR data as specified in Requirement R3 that meets the following: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] 4.1 A single record or multiple records that include: • A pre-trigger record length of at least two cycles and a total record length of at least 30-cycles for the same trigger point, or • At least two cycles of the pre-trigger data, the first three cycles of the post- trigger data, and the final cycle of the fault as seen by the fault recorder. 4.2 A minimum recording rate of 16 samples per cycle. 4.3 Trigger settings for at least the following: 4.3.1 Neutral (residual) overcurrent. 4.3.2 Phase undervoltage or overcurrent. | Possible | An uprate is unlikely to directly impact PRC-002 requirements, however the plant should verify that FR capabilities are restored once generator has returned to service following completion of uprate project work.
PRC-002-5 | R7. | R7. Each Generator Owner shall have DDR data to determine the following electrical quantities for each BES Element it owns for which it received notification as identified in Requirement R5: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] 7.1 One phase-to-neutral, phase-to-phase, or positive sequence voltage at either the generator step-up transformer (GSU) high-side or low-side voltage level. 7.2 The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R7, Part 7.1, phase current(s) for any phase-to-phase voltages, or positive sequence current. 7.3 Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. 7.4 Frequency of at least one of the voltages in Requirement R7, Part 7.1. | Possible | An uprate is unlikely to directly impact PRC-002 requirements, however the plant should verify that DDR capabilities are restored once generator has returned to service following completion of uprate project work.
PRC-002-5 | R8. | R8. Each Transmission Owner and Generator Owner responsible for DDR data for the BES Elements identified in Requirement R5 shall have continuous data recording and storage. If the equipment was installed prior to the effective date of the Reliability Standard PRC-002-23 and is not capable of continuous recording, triggered records must meet the following: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] 8.1. Triggered record lengths of at least three minutes. 8.2. At least one of the following three triggers: Off nominal frequency trigger set at: Low High o Eastern Interconnection <59.75 Hz >61.0 Hz o Western Interconnection <59.55 Hz >61.0 Hz o ERCOT Interconnection <59.35 Hz >61.0 Hz o Quebec Interconnection <58.55 Hz >61.5 Hz • Rate of change of frequency trigger set at: o Eastern Interconnection < -0.03125 Hz/sec >0.125 Hz/sec o Western Interconnection < -0.05625 Hz/sec >0.125 Hz/sec o ERCOT Interconnection < -0.08125 Hz/sec >0.125 Hz/sec o Quebec Interconnection < -0.18125 Hz/sec >0.1875 Hz/sec • Undervoltage trigger set no lower than 85 percent of normal operating voltage for a duration of 5 seconds. | Possible | An uprate is unlikely to directly impact PRC-002 requirements, however the plant should verify that DDR capabilities are restored once generator has returned to service.
PRC-002-5 | R9. | R9. Each Transmission Owner and Generator Owner responsible for DDR data for the BES Elements identified in Requirement R5 shall have DDR data that meet the following: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] 9.1 Input sampling rate of at least 960 samples per second. 9.2 Output recording rate of electrical quantities of at least 30 times per second. | Possible | An uprate is unlikely to impact PRC-002 requirements, however the plant should verify that DDR capabilities are restored once generator has returned to service.
PRC-005-6 | R1. | R1. Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems, Automatic Reclosing, and Sudden Pressure Relaying identified in Section 4.2, Facilities. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] The PSMP shall: 1.1. Identify which maintenance method (time-based, performance-based per PRC- 005 Attachment A, or a combination) is used to address each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. 1.2. Include the applicable monitored Component attributes applied to each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type consistent with the maintenance intervals specified in Tables 1- 1 through 1-5, Table 2, Table 3, Table 4-1 through 4-3, and Table 5 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components. | Possible | Each GO/GOP should perform a complete review of the PRC standards suite including PRC-005-6 if the entity introduces any new applicable components as part of the uprate process.
PRC-005-6 | R2. | R2. Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | Possible | Each GO/GOP should perform a complete review of the PRC standards suite including PRC-005-6 if the entity introduces any new applicable components as part of the uprate process.
PRC-005-6 | R3. | R3. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall maintain its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-3, and Table 5. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | Possible | Each GO/GOP should perform a complete review of the PRC standards suite including PRC-005-6 if the entity introduces any new applicable components as part of the uprate process.
PRC-005-6 | R4. | R4. Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the performancebased program(s). [Violation Risk Factor: High] [Time Horizon: Operations Planning] | Possible | Each GO/GOP should perform a complete review of the PRC standards suite including PRC-005-6 if the entity introduces any new applicable components as part of the uprate process.
PRC-012-2 | R1. | Prior to placing a new or functionally modified RAS in service or retiring an existing RAS, each RAS-entity shall provide the information identified in Attachment 1 for review to the Reliability Coordinator(s) where the RAS is located. | Possible | Each GO/GOP with a RAS should review whether the uprate will impact the design of the RAS and if so, assess compliance with PRC-012-2.
PRC-012-2 | R3. | Prior to placing a new or functionally modified RAS in service or retiring an existing RAS, each RAS‐entity that receives feedback from the reviewing Reliability Coordinator(s) identifying reliability issue(s) shall resolve each issue to obtain approval of the RAS from each reviewing Reliability Coordinator. | Possible | Each GO/GOP with a RAS should review whether the uprate will impact the design of the RAS and if so, assess compliance with PRC-012-2.
PRC-012-2 | R5. | Each RAS-entity, within 120 full calendar days of a RAS operation or a failure of its RAS to operate when expected, or on a mutually agreed upon schedule with its reviewing Reliability Coordinator(s), shall: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] 5.1. Participate in analyzing the RAS operational performance to determine whether: 5.1.1. The System events and/or conditions appropriately triggered the RAS. 5.1.2. The RAS responded as designed. 5.1.3. The RAS was effective in mitigating BES performance issues it was designed to address. 5.1.4. The RAS operation resulted in any unintended or adverse BES response. 5.2. Provide the results of RAS operational performance analysis that identified any deficiencies to its reviewing Reliability Coordinator(s). | Possible | Each GO/GOP with a RAS should review whether the uprate will impact the design of the RAS and if so, assess compliance with PRC-012-2.
PRC-012-2 | R8. | Each RAS-entity shall participate in performing a functional test of each of its RAS to verify the overall RAS performance and the proper operation of non-Protection System components: [Violation Risk Factor: High] [Time Horizon: Long-term Planning] • At least once every six full calendar years for all RAS not designated as limited impact, or • At least once every twelve full calendar years for all RAS designated as limited impact | Possible | Each GO/GOP with a RAS should review whether the uprate will impact the design of the RAS and if so, assess compliance with PRC-012-2.
PRC-017-1 | R1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have a system maintenance and testing program(s) in place. The program(s) shall include: | Possible | Each GO/GOP with a RAS should review whether the uprate will impact the design of the RAS and if so, assess compliance with PRC-017-1.
PRC-017-1 | R2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall provide documentation of the program and its implementation to the appropriate Regional Reliability Organizations and NERC on request (within 30 calendar days). | Possible | Each GO/GOP with a RAS should review whether the uprate will impact the design of the RAS and if so, assess compliance with PRC-017-1.
PRC-019-2 | R2. | Within 90 calendar days following the identification or implementation of systems, equipment or setting changes that will affect the coordination described in Requirement R1, each Generator Owner and Transmission Owner with applicable Facilities shall perform the coordination as described in Requirement R1. These possible systems, equipment or settings changes include, but are not limited to the following: • Voltage regulating settings or equipment changes; • Protection System settings or component changes; • Generating or synchronous condenser equipment capability changes; or • Generator or synchronous condenser step-up transformer changes. | Possible | Each GO/GOP should evaluate whether the uprate involves the implementation of systems, equipment, or settings changes that will require coordination under R1.
PRC-023-6 | R1. | R1. Each Transmission Owner, Generator Owner, and Distribution Provider shall use any one of the following criteria (Requirement R1, criteria 1 through 13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the BES for all fault conditions. Each Transmission Owner, Generator Owner, and Distribution Provider shall evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees. [Violation Risk Factor: High] [Time Horizon: Long Term Planning] Criteria: 1. Set transmission line relays so they do not operate at or below 150% of the highest seasonal Facility Rating of a circuit, for the available defined loading duration nearest 4 hours (expressed in amperes). 2. Set transmission line relays so they do not operate at or below 115% of the highest seasonal 15-minute Facility Rating1 of a circuit (expressed in amperes). 3. Set transmission line relays so they do not operate at or below 115% of the maximum theoretical power transfer capability (using a 90-degree angle between the sending-end and receiving-end voltages and either reactance or complex impedance) of the circuit(expressed in amperes) using one of the following to perform the power transfer calculation: • An infinite source (zero source impedance) with a 1.00 per unit bus voltage at each end of the line. • An impedance at each end of the line, which reflects the actual system source impedance with a 1.05 per unit voltage behind each source impedance. 4. Set transmission line relays on series compensated transmission lines so they do not operate at or below the maximum power transfer capability of the line, determined as the greaterof: • 115% of the highest emergency rating of the series capacitor. • 115% of the maximum power transfer capability of the circuit (expressed in amperes), calculated in accordance with Requirement R1, criterion 3, using the full lineinductive reactance. 5. Set transmission line relays on weak source systems so they do not operate at or below 170% of the maximum end-of-line three-phase fault magnitude (expressed in amperes). 6. Reserved 7. Set transmission line relays applied at the load center terminal, remote from generation stations, so they do not operate at or below 115% of the maximum current flow from the load to the generation source under any system configuration. 1 When a 15-minute rating has been calculated and published for use in real-time operations, the 15-minute rating can be used to establish the loadability requirement for the protective relays. 8. Set transmission line relays applied on the bulk system-end of transmission lines that serve load remote to the system so they do not operate at or below 115% of the maximum current flow from the system to the load under any system configuration. 9. Set transmission line relays applied on the load-end of transmission lines that serve load remote to the bulk system so they do not operate at or below 115% of the maximum current flow from the load to the system under any system configuration. 10. Set transformer fault protection relays and transmission line relays on transmission lines terminated only with a transformer so that the relays do not operate at or below the greater of: • 150% of the applicable maximum transformer nameplate rating (expressed in amperes), including the forced cooled ratings corresponding to all installed supplemental cooling equipment. • 115% of the highest operator established emergency transformer rating. 10.1 Set load-responsive transformer fault protection relays, if used, such that the protection settings do not expose the transformer to a fault level and duration that exceeds the transformer’s mechanical withstand capability2. 11. For transformer overload protection relays that do not comply with the loadability component of Requirement R1, criterion 10 set the relays according to one of the following: • Set the relays to allow the transformer to be operated at an overload level of at least 150% of the maximum applicable nameplate rating, or 115% of the highest operator established emergency transformer rating, whichever is greater, for at least 15 minutesto provide time for the operator to take controlled action to relieve the overload. • Install supervision for the relays using either a top oil or simulated winding hot spot temperature element set no less than 100° C for the top oil temperature or no lessthan 140° C for the winding hot spot temperature3. 12. When the desired transmission line capability is limited by the requirement to adequately protect the transmission line, set the transmission line distance relays to a maximum of 125% of the apparent impedance (at the impedance angle of the transmission line) subject to the following constraints: a. Set the maximum torque angle (MTA) to 90 degrees or the highest supported by the manufacturer. b. Evaluate the relay loadability in amperes at the relay trip point at 0.85 per unit voltage and a power factor angle of 30 degrees. c. Include a relay setting component of 87% of the current calculated in 2 As illustrated by the “dotted line” in IEEE C57.109-1993 - IEEE Guide for Liquid-Immersed Transformer Through-Fault-Current Duration, Clause 4.4, Figure 4. 3 IEEE standard C57.91, Tables 7 and 8, specify that transformers are to be designed to withstand a winding hot spot temperature of 180 degrees C, and Annex A cautions that bubble formation may occur above 140 degrees C. PRC-023-6 – Transmission Relay Loadability Page 5 of 17 Requirement R1, criterion 12 in the Facility Rating determination for the circuit. 13. Where other situations present practical limitations on circuit capability, set the phase protection relays so they do not operate at or below 115% of such limitations. | Possible | This would need to be reevaluated by the entity. An uprate would likely result in Protection System settings changes which would need verified for compliance against PRC-023 requirements.
PRC-023-6 | R3. | R3. Each Transmission Owner, Generator Owner, and Distribution Provider that uses a circuit capability with the practical limitations described in Requirement R1, criterion 7, 8, 9, 12, or 13 shall use the calculated circuit capability as the Facility Rating of the circuit and shall obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. [Violation Risk Factor: Medium] [Time Horizon: Long Term Planning] | Possible | This would need to be reevaluated by the entity. An uprate would likely result in Protection System settings changes which would need verified for compliance against PRC-023 requirements.
PRC-023-6 | R4. | R4. Each Transmission Owner, Generator Owner, and Distribution Provider that chooses to use Requirement R1 criterion 2 as the basis for verifying transmission line relay loadability shall provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays at least once each calendar year, with no more than 15 months between reports. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning] | Possible | This would need to be reevaluated by the entity. An uprate would likely result in Protection System settings changes which would need verified for compliance against PRC-023 requirements.
PRC-023-6 | R5. | R5. Each Transmission Owner, Generator Owner, and Distribution Provider that sets transmission line relays according to Requirement R1 criterion 12 shall provide an updated list of the circuits associated with those relays to its Regional Entity at least once each calendar year, with no more than 15 months between reports, to allow the PRC-023-6 – Transmission Relay Loadability Page 6 of 17 ERO to compile a list of all circuits that have protective relay settings that limit circuit capability. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning] | Possible | This would need to be reevaluated by the entity. An uprate would likely result in Protection System settings changes which would need verified for compliance against PRC-023 requirements.
PRC-024-4 | R1. | R1. Each Generator Owner and Transmission Owner shall set applicable frequency protection [4] in accordance with PRC-024-4 Attachment 1 such that the applicable protection does not cause the Facility to which it is applied to trip within the “no trip zone” during a frequency excursion with the following exceptions: • Applicable frequency protection may be set to trip within a portion of the “no trip zone” for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. [4] Frequency, voltage, and volts per hertz protection (whether provided by relaying or functions within associated control systems) that respond to electrical signals and: (i) directly trip the synchronous generator(s), type 1 or type 2 wind resource(s), or synchronous condenser(s); or (ii) provide signals to trip the same Facilities. | Possible | Entity should verify PRC-024 compliance after an uprate.
PRC-024-4 | R2. | R2. Each Generator Owner and Transmission Owner shall set applicable voltage protection [5] in accordance with PRC-024-4 Attachment 2, such that the applicable protection does not cause the Facility to which it is applied to trip within the “no trip zone” during a voltage excursion at the high-side of the GSU or MPT, subject to the following exceptions: • If the Transmission Planner allows less stringent voltage protection settings than those required to meet PRC-024-4 Attachment 2, then the Generator Owner or Transmission Owner may set its protection within the voltage recovery characteristics of a location-specific Transmission Planner’s study. • Applicable voltage protection may be set to trip during a voltage excursion within a portion of the “no trip zone” for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. [5] Frequency, voltage, and volts per hertz protection (whether provided by relaying or functions within associated control systems) that respond to electrical signals and: (i) directly trip the synchronous generator(s), type 1 or type 2 wind resource(s), or synchronous condenser(s); or (ii) provide signals to trip the same Facilities. | Possible | Entity should verify PRC-024 compliance after an uprate.
PRC-024-4 | R3. | R3. Each Generator Owner and Transmission Owner shall document each known regulatory or equipment limitation [6] that prevents its Facility, with applicable frequency or voltage protection from meeting the protection setting criteria in Requirements R1 or R2, including (but not limited to) study results, experience from an actual event, or manufacturer’s advice. [6] Excludes limitations caused by the setting capability of the frequency, voltage, and volts per hertz protective relays applied to the synchronous generator(s), type 1 and type 2 wind resource(s), and synchronous condenser(s). This does not exclude limitations originating in the equipment protected by the relay(s). R3.1 The Generator Owner and Transmission Owner shall communicate the documented regulatory or equipment limitation, or the removal of a previously documented regulatory or equipment limitation, to its Planning Coordinator and Transmission Planner within 30 calendar days of any of the following: • Identification of a regulatory or equipment limitation. • Repair of the equipment causing the limitation that removes the limitation. • Replacement of the equipment causing the limitation with equipment that removes the limitation. • Creation or adjustment of an equipment limitation caused by consumption of the cumulative turbine life-time frequency excursion allowance. | Possible | Entity would need to verify PRC-024 compliance after an uprate.
PRC-025-2 | R1. | Each Generator Owner, Transmission Owner, and Distribution Provider shall apply settings that are in accordance with PRC-025-2 – Attachment 1: Relay Settings, on each load-responsive protective relay while maintaining reliable fault protection. [Violation Risk Factor: High] [Time Horizon: Long-Term Planning] | Possible | Entity should verify settings are correct following the execution of an uprate.
PRC-027-1 | R1. | R1. Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a process for developing new and revised Protection System settings for BES Elements, such that the Protection Systems operate in the intended sequence during Faults. The process shall include: [Violation Risk Factor: Medium] [Time Horizon: Long‐term Planning] 1.1. A review and update of short‐circuit model data for the BES Elements under study. 1.2. A review of the developed Protection System settings. 1.3. For Protection System settings applied on BES Elements that electrically join Facilities owned by separate functional entities (Transmission Owners, Generator Owners, and Distribution Providers), provisions to: 1.3.1. Provide the proposed Protection System settings to the owner(s) of the electrically joined Facilities. 1.3.2. Respond to any owner(s) that provided its proposed Protection System settings pursuant to Requirement R1, Part 1.3.1 by identifying any coordination issue(s) or affirming that no coordination issue(s) were identified. 1.3.3. Verify that identified coordination issue(s) associated with the proposed Protection System settings for the associated BES Elements are addressed prior to implementation. 1.3.4. Communicate with the other owner(s) of the electrically joined Facilities regarding revised Protection System settings resulting from unforeseen circumstances that arise during implementation or commissioning, Misoperation investigations, maintenance activities, or emergency replacements required as a result of Protection System component failure. | Possible | The entity should review whether the uprate will result in a change to existing Protections settings, and if so, assure those changes are executed in accordance with PRC-027-1
PRC-027-1 | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider shall, for each BES Element with Protection System functions identified in Attachment A: • Option 1: Perform a Protection System Coordination Study in a time interval not to exceed six-calendar years; or • Option 2: Compare present Fault current values to an established Fault current baseline and perform a Protection System Coordination Study when the comparison identifies a 15 percent or greater deviation in Fault current values (either three phase or phase to ground) at a bus to which the BES Element is connected, all in a time interval not to exceed six-calendar years; or, • Option 3: Use a combination of the above. | Possible | In the instance of adding a new steam cycle (and the entity was using Option 2) it could change their available fault current and trigger a new Protection System Coordination Study.
PRC-027-1 | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider shall utilize its process established in Requirement R1 to develop new and revised Protection System settings for BES Elements. | Possible | The entity should review whether the uprate will result in a change to existing Protections settings, and if so, assure those changes are executed in accordance with PRC-027-1
PRC-028-1 | R1. | R1. Each Generator Owner shall have sequence of event recording (SER) data for the following Elements that it owns: [Violation Risk Factor: Lower] [Time Horizon: Longterm Planning] 1.1. Circuit breaker position (open/close) for circuit breakers associated with the main power transformer(s)1, collector bus(es), shunt static and dynamic reactive device(s), and AC-DC and DC-AC converters, if any, in case of VSC HVDC system with a dedicated connection to Inverter-Based Resource. 1.2. For IBR units2 in commercial operation3 after the effective date of this standard, the following data shall be recorded when triggered by ride-through operation or tripping of an IBR unit. 1.2.1. All fault codes. 1.2.2. All fault alarms. 1.2.3. High and low voltage ride-through mode status. 1.2.4. High and low frequency ride-through mode status. 1.3. For IBR units in commercial operation before the effective date of this standard, if capable, the following data shall be recorded when triggered by ride-through operation or tripping of an IBR unit. 1.3.1. All fault codes. 1.3.2. All fault alarms. 1.3.3. High and low voltage ride-through mode status. 1.3.4. High and low frequency ride-through mode status. | Possible | An uprate is unlikely to impact PRC-028 requirements, however the IBR facility should verify that SER capabilities are restored once generator has returned to service.
PRC-028-1 | R2. | R2. Each Generator Owner shall have triggered fault recording (FR) data to determine the following electrical quantities for Elements that it owns: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] 2.1. High-side of the main power transformer FR data: 2.1.1. Phase-to-neutral voltage for each phase. 2.1.2. Each phase current and the residual or neutral current. 2.1.3. Real and Reactive Power expressed on a three-phase basis. 2.2. Collector feeder breaker FR data: 2.2.1. Phase-to-neutral voltage for each phase. 2.2.2. Each phase current and the residual or neutral current. 2.2.3. Real and Reactive Power expressed on a three-phase basis. 2.3. Shunt dynamic reactive device FR data: 2.3.1. Phase-to-neutral voltage for each phase. 2.3.2. Each phase current and the residual or neutral current. 2.3.3. Reactive Power output expressed on a three-phase basis. | Possible | An uprate is not likely to impact PRC-028 requirements, however the IBR facility should verify that FR capabilities are restored once generator has returned to service.
PRC-028-1 | R3. | R3. Each Generator Owner shall have FR data as specified in Requirement R2 that meets the following: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] 3.1. High-side of the main power transformer FR data: 3.1.1. A single record or multiple records that include a pre-trigger record length of at least two cycles and a total record length of at least 2.0 seconds for the same trigger point. 3.1.2. A minimum recording rate of 64 samples per cycle. 3.1.3. Trigger settings for at least the following: 3.1.3.1. Neutral (residual) overcurrent. 3.1.3.2. AC phase overvoltage and undervoltage. 3.1.3.3.Overfrequency and underfrequency 3.2. Collector feeder breaker FR data: 3.2.1. A single record or multiple records that include a pre-trigger record length of at least two cycles and a total record length of at least 2.0 seconds for the same trigger point. 3.2.2. A minimum recording rate of 64 samples per cycle. 3.2.3. Trigger settings for at least the following: 3.2.3.1. Neutral (residual) overcurrent, if applicable. 3.2.3.2. AC phase overvoltage and undervoltage. 3.2.3.3.Overfrequency and underfrequency. 3.3. Shunt dynamic reactive device FR data: 3.3.1. A single record or multiple records that include a pre-trigger record length of at least two cycles and a total record length of at least 2.0 seconds for the same trigger point. 3.3.2. A minimum recording rate of 64 samples per cycle. 3.3.3. Trigger settings for at least the following: 3.3.3.1. Neutral (residual) overcurrent. 3.3.3.2. AC phase overvoltage and undervoltage | Possible | An uprate is unlikely to impact PRC-028 requirements, however the IBR facility should verify that FR capabilities are restored once generator has returned to service.
PRC-028-1 | R4. | R4. Each Generator Owner shall have continuous dynamic disturbance recording (DDR) data and storage to determine the following electrical quantities for each main power transformer(s) it owns: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] 4.1. One phase-to-neutral or positive sequence voltage on high-side of the main power transformer(s). 4.2. The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R4, Part 4.1, or the positive sequence current. 4.3. Real Power and Reactive Power flows expressed on a three-phase basis corresponding to each main power transformer(s) where current measurements are required. 4.4. Frequency of any one of the voltage(s) in Requirement R4, Part 4.1. | Possible | An uprate is unlikely to impact PRC-028 requirements, however the IBR facility should verify that DDR capabilities are restored once generator has returned to service.
PRC-028-1 | R5. | Each Generator Owner responsible for DDR data for the electrical quantities identified in Requirement R4 shall have DDR data that meet the following: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] 5.1. Input sampling rate of at least 960 samples per second. 5.2. Output recording rate of electrical quantities of at least 60 times per second. | Possible | An uprate is unlikely to impact PRC-028 requirements, however the IBR facility should verify that DDR capabilities are restored once generator has returned to service.
PRC-028-1 | R6. | 6. Each Generator Owner shall time synchronize all SER, FR, and DDR data to meet the following: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] 6.1. Synchronization to Coordinated Universal Time (UTC) with or without a local time offset. 6.2. The IBR unit synchronized device clock accuracy within ± 100 milliseconds of UTC. For all other devices, synchronized device clock accuracy within ± 1 milliseconds of UTC. | Possible | An uprate is unlikely to impact PRC-028 requirements, however the IBR facility should verify that SER/FR/DDR capabilities are restored once generator has returned to service.
PRC-028-1 | R7. | R7. Each Generator Owner shall provide all requested SER, FR, and DDR data to its Transmission Planner, Planning Coordinator, Transmission Operator, Balancing Authority, Reliability Coordinator, Regional Entity, or NERC in accordance with the following: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] 7.1. Data shall be retrievable for the period of 20 calendar days, inclusive of the day the data was recorded. 7.2. Data subject to Part 7.1 shall be provided within 15 calendar days of a request unless an extension is granted by the requestor. 7.3. SER data shall be provided in ASCII4 Comma Separated Value (CSV) format following Attachment 1. 7.4. FR data shall be provided either in CSV format with appropriate headers or in electronic files that are formatted in conformance with C37.111, IEEE Standard Common Format for Transient Data Exchange (COMTRADE), revision C37.1111999 or later. 7.5. DDR data shall be provided either in CSV format with appropriate headers or in electronic files that are formatted in conformance with C37.111, IEEE Standard Common Format for Transient Data Exchange (COMTRADE), revision C37.1111999 or later. 7.6. Data files shall be named in conformance with C37.232, IEEE Standard for Common Format for Naming Time Sequence Data Files (COMNAME), revision C37.232-2011 or later. | Possible | An uprate is unlikely to impact PRC-028 requirements, however the IBR facility should verify that SER/FR/DDR capabilities are restored once generator has returned to service.
PRC-028-1 | R8. | R8. Each Generator Owner shall, upon the discovery of a failure of the recording capability for the SER, FR, or DDR data: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] • Restore the recording capability within 90 calendar days, or • Submit a Corrective Action Plan (CAP) to the Regional Entity within 90 calendar days and then implement it according to CAP timeline. | Possible | An uprate is unlikely to impact PRC-028 requirements, however the IBR facility should verify that SER/FR/DDR capabilities are restored once generator has returned to service.
PRC-029-1 | R1. | R1. Each Generator Owner shall ensure the design and operation is such that each IBR meets or exceeds Ride-through requirements, in accordance with the “must Ride-through[1] zone” as specified in Attachment 1, except in the following conditions: • The IBR needed to electrically disconnect in order to clear a fault; • The voltage at the high-side of the main power transformer[2] went outside an accepted hardware limitation, in accordance with Requirement R4; • The instantaneous positive sequence voltage phase angle change is more than 25 electrical degrees at the high-side of the main power transformer and is initiated by a non-fault switching event on the transmission system[3]; or • The Volts per Hz (V/Hz) at the high-side of the main power transformer exceed 1.1 per unit for longer than 45 seconds or exceed 1.18 per unit for longer than 2 seconds. [1] Includes no tripping associated with phase lock loop loss of synchronism. [2] For the purpose of this standard, the main power transformer is the power transformer that steps up voltage from the collection system voltage to the nominal transmission/interconnecting system voltage for IBRs. In case of IBR connecting via a dedicated Voltage Source Converter High Voltage Direct Current (VSC-HVDC), the main power transformer is the main power transformer on the receiving end. [3] Current blocking mode may be used for non-fault initiated phase jumps greater than 25 degrees in order to prevent tripping. | Possible | Entity should assess whether changes associated with the uprate impact the IBR's ride through settings.
PRC-029-1 | R2. | R2. Each Generator Owner shall ensure the design and operation is such that the voltage performance for each IBR adheres to the following during a voltage excursion, unless a documented hardware limitation exists in accordance with Requirement R4. 2.1 While the voltage at the high-side of the main power transformer remains within the continuous operation region as specified in Attachment 1, each IBR shall: 2.1.1 Continue to deliver the pre-disturbance level of Real Power or available Real Power[4], whichever is less.[5] [4] “Available Real Power" refers to changes of facility Real Power output attributed to factors such as weather patterns, change of wind, and change in irradiance, but not changes of facility Real Power attributed to IBR tripping in whole or part. [5] Except if this would occur during a frequency excursion. The Real Power response should recover in accordance with the primary frequency controller. 2.1.2 Continue to deliver Reactive Rower up to its Reactive Power limit and according to its controller settings. 2.1.3 Prioritize Real Power or Reactive Power when the voltage is less than 0.95 per unit, the voltage is within the continuous operating region, and the IBR cannot deliver both Real Power and Reactive Power due to a current limit or Reactive Power limit, unless otherwise specified through other mechanisms by an associated Transmission Planner, Planning Coordinator, Reliability Coordinator, or Transmission Operator. 2.2 While voltage at the high-side of the main power transformer is within the mandatory operation region as specified in Attachment 1, each IBR shall exchange current, up to the maximum capability to provide voltage support, on the affected phases during both symmetrical and asymmetrical voltage disturbances , either under[6]: • Reactive Power priority by default; or • Real Power priority if required through other mechanisms by an associated Transmission Planner, Planning Coordinator, Reliability Coordinator, or Transmission Operator [6] In either case and if required, the magnitude of Real Power and reactive current shall be as specified by the Transmission Planner, Planning Coordinator, Reliability Coordinator, or Transmission Operator. 2.3 While voltage at the high-side of the main power transformer is within the permissive operation region, as specified in Attachment 1, each IBR may operate in current blocking mode if necessary to avoid tripping. Otherwise, each IBR shall follow the requirements for the mandatory operation region in Requirement R2.2. 2.3.1 If an IBR enters current blocking mode, it shall restart current exchange in less than or equal to five cycles of positive sequence voltage returning to a continuous operation region or mandatory operation region. 2.4 Each IBR shall not itself cause voltage at the high-side of the main power transformer to exceed the applicable high voltage thresholds and time durations in its response as voltage recovers from the mandatory or permissive operation regions to the continuous operation region. 2.5 Each IBR shall restore Real Power output to the pre-disturbance or available level [7] (whichever is lesser) within 1.0 second when the voltage at the high-side of the main power transformer returns from the mandatory operation region or permissive operation region (including operating in current blocking mode) to the continuous operation region, as specified in Attachment 1, unless an associated Transmission Planner, Planning Coordinator, Reliability Coordinator, or Transmission Operator requires a lower post-disturbance Real Power level requirement or requires a different post-disturbance Real Power restoration time through other mechanisms.[8] [7] Except if this would occur during a frequency excursion. The Real Power response should recover in accordance with the primary frequency controller.[8] “Available Real Power" refers to changes of facility Real Power output attributed to factors such as weather patterns, change of wind, and change in irradiance, but not changes of facility Real Power attributed to IBR tripping in whole or part. | Possible | Entity should assess whether changes associated with the uprate impact the IBR's ability to ride-through during a frequency excursion event.
PRC-029-1 | R3. | R3. Each Generator Owner shall ensure the design and operation is such that each IBR meets or exceeds Ride-through requirements during a frequency excursion event whereby the System frequency remains within the “must Ride-through zone” according to Attachment 2 and the absolute rate of change of frequency (RoCoF)[9] magnitude is less than or equal to 5 Hz/second, unless a documented hardware limitation exists in accordance with Requirement R4. [ 9] Rate of change of frequency (RoCoF) is calculated as the average rate of change for multiple calculated system frequencies for a time period of greater than or equal to 0.1 second. RoCoF is not calculated during the fault occurrence and clearance. | Possible | Entity should assess whether changes associated with the uprate impact the IBR's ability to ride-through during a frequency excursion event.
VAR-002-4.1 | R1. | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following: [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations]  That the generator is being operated in start-up,1 shutdown,2 or testing mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or  That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. | Possible | An uprate is unlikely to have direct impacts; however, entities should verify that all voltage schedule monitoring/alarming and AVR/proper control mode is restored when the generator is returned to service.
VAR-002-4.1 | R2. | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule3 (within each generating Facility’s capabilities4) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] 2.1. When a generator’s AVR is out of service or the generator does not have an AVR, the Generator Operator shall use an alternative method to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. 2.2. When instructed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. 2.3. Generator Operators that do not monitor the voltage at the location specified in their voltage schedule shall have a methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | Possible | An uprate is unlikely to have direct impacts; however, entities should verify that all voltage schedule monitoring/alarming is restored when the generator is returned to service.
VAR-002-4.1 | R3. | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | Possible | An uprate is unlikely to have direct impacts; however, entities should verify that all voltage schedule status change alarming is restored when the generator is returned to service.
VAR-002-4.1 | R5. | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. [Violation Risk Factor: Lower] [Time Horizon: Real-time Operations] 5.1. For generator step-up and auxiliary transformers5 with primary voltages equal to or greater than the generator terminal voltage: 5.1.1. Tap settings. 5.1.2. Available fixed tap ranges. 5.1.3. Impedance data. | Possible | Entity should assess whether GSU tap settings were impacted as a part of the uprate process.
VAR-002-4.1 | R6. | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. [Violation Risk Factor: Lower] [Time Horizon: Real-time Operations] 6.1. If the Generator Owner cannot comply with the Transmission Operator’s specifications, the Generator Owner shall notify the Transmission Operator and shall provide the technical justification. | Possible | Entity should assess whether GSU tap settings were impacted as a part of the uprate process.

## Unique Situations to Consider
Standard | Requirement | Requirement Text | Impacted by Generator Uprate? | Analysis
EOP-005-3 | R11. | R11. Each Transmission Operator and each Generator Operator with a Blackstart Resource shall have written Blackstart Resource Agreements or mutually agreed upon procedures or protocols, specifying the terms and conditions of their arrangement. Such Agreements shall include references to the Blackstart Resource testing requirements. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | Possible | If the uprate involves changes to equipment associated with a Blackstart resource, it could impact agreements between TOP and GOP, which should be reviewed. | ReliabilityFirst disclaims any use of this sheet as being the complete universe of potentially implicated standards for all generator uprates or configuration changes. It is intended as a useful tool in starting your compliance analysis, when considering a generator uprate.
EOP-005-3 | R12. | R12. Each Generator Operator with a Blackstart Resource shall have documented procedures for starting each Blackstart Resource and energizing a bus. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | Possible | If the uprate involves changes to equipment associated with a Blackstart resource, the entity should review its procedures for starting each Blackstart Resource to assure any necessary changes are captured.
EOP-005-3 | R13. | R13. Each Generator Operator with a Blackstart Resource shall notify its Transmission Operator of any known changes to the capabilities of that Blackstart Resource affecting the ability to meet the Transmission Operator’s restoration plan within 24 hours following such change. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | Possible | Assuming implementing an uprate would make the generator unavailable for some period of time, the entity needs to communicate the capability impact to the TOP.
EOP-005-3 | R14. | R14. Each Generator Operator with a Blackstart Resource shall perform Blackstart Resource tests, and maintain records of such testing, in accordance with the testing requirements set by the Transmission Operator to verify that the Blackstart Resource can perform as specified in the restoration plan. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] 14.1. Testing records shall include at a minimum: name of the Blackstart Resource, unit tested, date of the test, duration of the test, time required to start the unit, an indication of any testing requirements not met under Requirement R7. 14.2. Each Generator Operator shall provide the blackstart test results within 30 calendar days following a request from its Reliability Coordinator or Transmission Operator. | Possible | An entity that modifies a Blackstart resource should review the TOPs testing requirements to see if new tests are required.
EOP-012-3 | R1. | R1. At least once every five (5) calendar years, each Generator Owner shall, for each of its applicable generating unit(s): [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] 1.1. Calculate the Extreme Cold Weather Temperature for each of its applicable generating unit(s) and identify the calculation date, source(s) of temperature data, and adjustments utilized for missing or invalid hourly temperature data, if necessary; and 1.1.1. If the recalculated Extreme Cold Weather Temperature is lower than the previous Extreme Cold Weather Temperature, the entity shall review and update its cold weather preparedness plan(s) under Requirement R4 within six (6) calendar months of the recalculation, and if new corrective actions are needed to provide the required operational capability described in Requirement R2 or R3, the entity shall develop a Corrective Action Plan within six (6) calendar months of the recalculation. 1.2. Identify generating unit(s) cold weather data, to include: 1.2.1. Generating unit(s) operating limitations in cold weather to include: 1.2.1.1. Capability and availability; 1.2.1.2. Fuel supply and inventory concerns; 1.2.1.3. Start-up issues; 1.2.1.4. Fuel switching capabilities; and 1.2.1.5. Environmental constraints. 1.2.2. Generating unit(s) minimum: • Design temperature, and if available, the concurrent wind speed and precipitation; • Historical operating temperature at least one hour in duration, and if available, the concurrent wind speed and precipitation; or • Current cold weather performance temperature determined by an engineering analysis, which includes the concurrent wind speed and precipitation. | Possible | Depending on the nature of the uprate, updates to EOP-012 documentation could be required - particularly if the fuel type has been modified or another fuel type added (e.g., addition of steam cycle).
EOP-012-3 | R2. | R2. Applicable to generating units that begin commercial operation¹ on or after October 1, 2027²: Each Generator Owner, for each generating unit that has a calculated Extreme Cold Weather Temperature at or below 32 degrees Fahrenheit (zero degrees Celsius) as determined in Requirement R1, and that self-commits or is required to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius),³ shall: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning, Operations Planning] • Implement freeze protection measures to protect Generator Cold Weather Critical Components that provide the capability to operate at the generating unit(s)’ Extreme Cold Weather Temperature with sustained concurrent twenty (20) mph (32 km/h) wind speed for (i) a period of not less than twelve (12) continuous hours, or (ii) the maximum operational duration for intermittent energy resources if less than twelve (12) continuous hours; or • Document in a declaration, with justification, if applicable, a Generator Cold Weather Constraint in accordance with Requirement R8. | Possible | Depending on the nature of the uprate, new or different freeze protection measures may be required.
EOP-012-3 | R3. | R3. Applicable to generating unit(s) in commercial operation prior to October 1, 2027:⁴Each Generator Owner, for each generating unit that has a calculated Extreme Cold Weather Temperature at or below 32 degrees Fahrenheit (zero degrees Celsius) as determined in Requirement R1, and that self-commits or is required to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius),⁵ shall: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning, Operations Planning] • Implement freeze protection measures to protect Generator Cold Weather Critical Components that provide the capability to operate at the generating unit(s)' Extreme Cold Weather Temperature; or • Develop a Corrective Action Plan to add new or modify existing freeze protection measures to provide the capability to operate at the generating unit(s)' Extreme Cold Weather Temperature. | Possible | Depending on the nature of the uprate, new freeze protection measures could be different.
EOP-012-3 | R4. | R4. Each Generator Owner shall implement and maintain one or more cold weather preparedness plan(s) for its generating units. The cold weather preparedness plan(s) shall include the following, at a minimum: [Violation Risk Factor: High] [Time Horizon: Operations Planning and Real-time Operations] 4.1. The lowest calculated Extreme Cold Weather Temperature for each generating unit, as determined in Requirement R1;⁶ 4.2. The generating unit cold weather data, as determined in Requirement R1, Part 1.2; 4.3. Documentation identifying Generator Cold Weather Critical Components; 4.4. Documentation of freeze protection measures implemented on Generator Cold Weather Critical Components that includes measures used to reduce the cooling effects of wind determined necessary by the Generator Owner to protect against heat loss, and where applicable, the effects of freezing precipitation (e.g., sleet, snow, ice, and freezing rain); 4.5. Annual inspection and maintenance of generating unit(s) freeze protection measures implemented on Generator Cold Weather Critical Components. | Possible | Depending on the nature of the uprate, updates to EOP-012 changes in documentation could be required - particularly if the fuel type has been modified or another fuel type added (e.g., addition of steam cycle).
EOP-012-3 | R5. | R5. Each Generator Owner, in conjunction with its Generator Operator, shall identify the entity responsible for providing generating unit-specific training, and that identified entity shall provide annual training to the maintenance and operations personnel, as applicable, responsible for implementing the cold weather preparedness plan(s) developed pursuant to Requirement R4. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning, Operations Planning] | Possible | Depending on the nature of the uprate, the entity may need to revise its training materials to address changes to its Cold Weather Preparedness Plan.
FAC-001-4 | R2. | R2. Each applicable Generator Owner shall document Facility interconnection requirements and make them available upon request within 45 calendar days of full execution of an Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | Possible | In a unique circumstance where a third party is interconnecting at the GO's facilities as part of the uprate, the entity should review FAC-001-4 and whether it is implicated.
FAC-001-4 | R4. | Each applicable Generator Owner shall address the following items in its Facility interconnection requirements: [Violation Risk Factor: Lower] [Time Horizon: Long-Term Planning] 4.1. Procedures for coordinated studies of new interconnections and their impacts on affected system(s). FAC-001-4 — Facility Interconnection Requirements 4.2. Procedures for notifying those responsible for the reliability of affected system(s) of new interconnections. 4.3. Procedures for confirming with those responsible for the reliability of affected systems that new Facilities or existing Facilities seeking to make a qualified change as defined by the Planning Coordinator are within a Balancing Authority Area. | Possible | In a unique circumstance where a third party is interconnecting at the GO's facilities as part of the uprate, the entity should review FAC-001-4 and whether it is implicated.
FAC-003-5 | R1. | R1. Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the Minimum Vegetation Clearance Distance (MVCD) of its applicable line(s), operating within their Rating and all Rated 1.1. An encroachment into the MVCD as shown in FAC‐003‐Table 2, observed in Real‐ time, absent a Sustained Outage,5 1.2. An encroachment due to a fall‐in from inside the ROW that caused a vegetation‐ related Sustained Outage,6 1.3. An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation‐related Sustained Outage,7 1.4. An encroachment due to vegetation growth into the MVCD that caused a vegetation‐related Sustained Outage. | Possible | In rare circumstances where the uprate impacts the rating of the intertie, it could require additional vegetation clearances under FAC-003-5.
IRO-010-5 | R3. | R3. Each Reliability Coordinator, Balancing Authority, Generator Owner, Generator Operator, Transmission Operator, Transmission Owner, and Distribution Provider receiving a specification(s) in Requirement R2 shall satisfy the obligations of the documented specifications . (Violation Risk Factor: Medium) (Time Horizon: Operations Planning, Same-Day Operations, Real-time Operations) | Possible | A generator uprate is unlikely to change the nature of the information a GO/GOP would need to provide. But for instance, if an additional transformer was added the entity would need to ensure properly telemetry was implemented.
NUC-001-4 | R1. | The Nuclear Plant Generator Operator shall provide the proposed NPIRs in writing to the applicable Transmission Entities and shall verify receipt. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning ] | Possible | All aspects of NUC-001 would need to be revisited if a nuclear plant is pursuing an uprate.
NUC-001-4 | R2. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall have in effect one or more Agreements[1] that include mutually agreed to NPIRs and document how the Nuclear Plant Generator Operator and the applicable Transmission Entities shall address and implement these NPIRs. | Possible | All aspects of NUC-001 would need to be revisited if a nuclear plant is pursuing an uprate.
NUC-001-4 | R3. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator.: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning ] | Possible | All aspects of NUC-001 would need to be revisited if a nuclear plant is pursuing an uprate.
NUC-001-4 | R4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall [Violation Risk Factor: High] [Time Horizon: Operations Planning and Real-time Operations] 4.1. Incorporate the NPIRs into their operating analyses of the electric system. 4.2. Operate the electric system to meet the NPIRs. 4.3. Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. | Possible | All aspects of NUC-001 would need to be revisited if a nuclear plant is pursuing an uprate.
NUC-001-4 | R5. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall operate the nuclear plant to meet the NPIRs. [Violation Risk Factor: High] [Time Horizon: Operations Planning and Real-time Operations ] | Possible | All aspects of NUC-001 would need to be revisited if a nuclear plant is pursuing an uprate.
NUC-001-4 | R6. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities and the Nuclear Plant Generator Operator shall coordinate outages and maintenance activities which affect the NPIRs. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | Possible | All aspects of NUC-001 would need to be revisited if a nuclear plant is pursuing an uprate.
NUC-001-4 | R7. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall inform the applicable Transmission Entities of actual or proposed changes to nuclear plant design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Violation Risk Factor: High] [Time Horizon: | Possible | All aspects of NUC-001 would need to be revisited if a nuclear plant is pursuing an uprate.
NUC-001-4 | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Violation Risk Factor: High] [Time Horizon: Long-term Planning] | Possible | All aspects of NUC-001 would need to be revisited if a nuclear plant is pursuing an uprate.
NUC-001-4 | R9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include the following elements in aggregate within the Agreement(s) identified in R2.  Where multiple Agreements with a single Transmission Entity are put into effect, the R9 elements must be addressed in aggregate within the Agreements; however, each Agreement does not have to contain each element. The Nuclear Plant Generator Operator and the Transmission Entity are responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements.  Where Agreements with multiple Transmission Entities are required, the Nuclear Plant Generator Operator is responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements with the Transmission Entities. The Agreements with each Transmission Entity do not have to contain each element; however, the Agreements with the multiple Transmission Entities, in the aggregate, must address all R9 elements. For each Agreement(s), the Nuclear Plant Generator Operator and the Transmission Entity are responsible to ensure the Agreement(s) contain(s) the elements of R9 applicable to that Transmission Entity. : [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] 9.1. Retired. [Note: Part 9.1 was retired under the Paragraph 81 project. The NUC SDT proposes to leave this Part blank to avoid renumbering Requirement parts that would impact existing agreements throughout the industry.] 9.2. Technical requirements and analysis: 9.2.1. Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the Agreement. 9.2.2. Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. 9.2.3. Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. 9.3. Operations and maintenance coordination 9.3.1. Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. 9.3.2. Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. 9.3.3. Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. 9.3.4. Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. 9.3.5. Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. 9.3.6. Coordination of physical and cyber security protection at the nuclear plant interface to ensure each asset is covered under at least one entity’s plan. 9.3.7. Coordination of the NPIRs with transmission system Remedial Action Schemes and any programs that reduce or shed load based on underfrequency or undervoltage. 9.4. Communications and training Administrative elements: 9.4.1. Provisions for communications affecting the NPIRs between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of applicable unique terms. 9.4.2. Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. 9.4.3. Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. 9.4.4. Provisions for supplying information necessary to report to government agencies, as related to NPIRs. 9.4.5. Provisions for personnel training, as related to NPIRs. | Possible | All aspects of NUC-001 would need to be revisited if a nuclear plant is pursuing an uprate.
PRC-026-2 | R2. | R2. Each Generator Owner and Transmission Owner shall: [Violation Risk Factor: High] [Time Horizon: Operations Planning] 2.1 Within 12 full calendar months of notification of a BES Element pursuant to Requirement R1, determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-2 – Attachment B where an evaluation of that Element’s load-responsive protective relay(s) based on PRC-026-2 – Attachment B criteria has not been performed in the last five calendar years. 2.2 Within 12 full calendar months of becoming aware² of a generator, transformer, or transmission line BES Element that tripped in response to a stable or unstable³ power swing due to the operation of its protective relay(s), determine whether its protective relay(s) applied to that BES Element meets thecriteria in PRC-026-2 – Attachment B. | Possible | Changes to the generator could result in the PC identifying that the generator has an angular constraint, triggering PRC-026 requirements.
PRC-026-2 | R3. | R3. Each Generator Owner and Transmission Owner shall, within six full calendar months of determining a load-responsive protective relay does not meet the PRC-026-2 – Attachment B criteria pursuant to Requirement R2, develop a Corrective Action Plan (CAP) to meet one of the following: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] • The Protection System meets the PRC-026-2 – Attachment B criteria, while maintaining dependable fault detection and dependable out-of-step tripping (if out- of-step tripping is applied at the terminal of the BES Element); or • The Protection System is excluded under the PRC-026-2 – Attachment A criteria (e.g., modifying the Protection System so that relay functions are supervised by power swing blocking or using relay systems that are immune to power swings), while maintaining dependable fault detection and dependable out-of-step tripping (if out-of-step tripping is applied at the terminal of the BES Element). | Possible | Changes to the generator could result in the PC identifying that the generator has an angular constraint, triggering PRC-026 requirements.
PRC-026-2 | R4. | R4. Each Generator Owner and Transmission Owner shall implement each CAP developed pursuant to Requirement R3 and update each CAP if actions or timetables change until all actions are complete. [Violation Risk Factor: Medium][Time Horizon: Long-Term Planning] | Possible | Changes to the generator could result in the PC identifying that the generator has an angular constraint, triggering PRC-026 requirements.
TPL-007-4 | R6. | R6. Each Transmission Owner and Generator Owner shall conduct a benchmark thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater. The benchmark thermal impact assessment shall: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] 6.1. Be based on the effective GIC flow information provided in Requirement R5; 6.2. Document assumptions used in the analysis; 6.3. Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and 6.4. Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. | Possible | An uprate alone is unlikely to impact a GIC study. However if changes are made to any existing transformers (or additional transformers added), it could modify TPL-007 study results and potentially impact GIC values.
TPL-007-4 | R10. | R10. Each Transmission Owner and Generator Owner shall conduct a supplemental thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater. The supplemental thermal impact assessment shall: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] 10.1. Be based on the effective GIC flow information provided in Requirement R9; 10.2. Document assumptions used in the analysis; 10.3. Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and 10.4. Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. | Possible | An uprate alone is unlikely to result in changes. However if changes are made to any existing transformers (or additional transformers added), it could modify TPL-007 study results and potentially alter GIC values.