## Instructions
Contains Confidential Information Including Privileged and Critical Energy Infrastructure Information. Do Not Distribute. Attachment C - Data Sampling Request | [5 empty] | Updated: 11/1/2025
Standard Number | Requirement Number | Data List | Data List returned to ReliabilityFirst | Evidence Requested | Evidence Returned to ReliabilityFirst
VAR-002-4.1 | R2. | Provide a list of units and dates they were on-line and were not exempted by the TOP from maintaining the generator voltage or Reactive Power output (within applicable Facility Ratings) as directed by the Transmission Operator. NOTE: If units are peakers or do not run all the time provide dates for current and previous years that units were on-line. NOTE: If units are always on-line provide a list of units. Use Included Template | Return Data List to ReliabilityFirst no later than the deadline indicated in the Notification Letter for "Submittal of Attachment C - Data Sampling." | The Generator Operator shall have evidence to show that it notified its associated Transmission Operator any time it failed to operate a generator in the automatic voltage control mode or in a different control mode as specified in Requirement R1. If a generator is being started up or shut down with the automatic voltage control off, or is being tested, and no notification of the AVR status is made to the Transmission Operator, the Generator Operator will have evidence that it notified the Transmission Operator of its procedure for placing the unit into automatic voltage control mode as required in Requirement R1. Such evidence may include, but is not limited to, dated evidence of transmittal of the procedure such as an electronic message or a transmittal letter with the procedure included or attached. If a generator is exempted, the Generator Operator shall also have evidence that the generator is exempted from being in automatic voltage control mode (with its AVR in service and controlling voltage). | Return evidence to ReliabilityFirst no later than the deadline indicated in the Notification Letter for "Submittal of Attachment B, the RSAWs, Data Sampling Evidence, and all evidence of compliance."

## VAR-002-4.1 R2
Index Number (Add more as needed) | Generation Station | Unit | Dates on-line (this is only relevant if units are peakers or do not run a lot of the time) Provide dates for current and previous year | Connection (Ex: 13.8/138) | Comments
1
2
3
4
5
6
7
8
9
10

## Day-Worksheet
This worksheet can be used to convey your VAR-002-4.1 R2 evidence in ten minute increments that you are following your voltage schedule. Please copy this sheet as needed for all samples required.
Complete all fields highlighted in yellow.
Sample: | 1
Day: | Friday, March 13, 2020
Unit: | ABC Unit
Voltage Schedule
|  |  | If voltage schedule varies throughout the day copy the actual voltage schedule into rows 11 - 154 that corresponds to that time period |  | If Voltage is > High Limit or < Low Limit, it will be flagged RED that you are outside your voltage schedule. Please provide an explanation below for all instances you are outside your voltage schedule (e.g. TOP Exception, outside of Generator Capabilities, etc.) Audit Team will follow-up for additional evidence proving the exception, capabilities, etc. | Use Column G, H, I for additional information that you may want to communicate to the audit team. This may include MVAR output, AVR status (On/Off), 4 kV bus voltage, GSU tap setting, to show that you were controlling voltage at the station within capabilities. Additional information is not needed when the unit is inside the voltage schdule
|  |  | High Voltage Schedule (kV) | Low Voltage Schedule (kV)
Time: | Voltage | MW Output of Unit | 142 | 136
0:00 | 138.5 | 250 | 142 | 136
0:10 | 138.6 | 252 | 142 | 136
0:20 | 138.7 | 253 | 142 | 136
0:30 | 138.8 | 254 | 142 | 136
0:40 | 140 | 253 | 142 | 136
0:50 | 140.2 | 252 | 142 | 136
1:00 | 141 | 253 | 142 | 136
1:10 | 141.5 | 250 | 142 | 136
1:20 | 141 | 252 | 142 | 136
1:30 | 139.5 | 253 | 142 | 136
1:40 | 139.4 | 254 | 142 | 136
1:50 | 139.3 | 253 | 142 | 136
2:00 | 139.2 | 252 | 142 | 136
2:10 | 138.9 | 253 | 142 | 136
2:20 | 138.5 | 250 | 142 | 136
2:30 | 145 | 252 | 142 | 136 | Contacted TOP. Exception granted due to line tripping outside of our system. AVR responded to go back within voltage schedule within timely manner.
2:40 | 138.1 | 253 | 142 | 136
2:50 | 137.5 | 254 | 142 | 136
3:00 | 137.3 | 253 | 142 | 136
3:10 | 137.1 | 252 | 142 | 136
3:20 | 136.4 | 253 | 142 | 136
3:30 | 136.3 | 250 | 142 | 136
3:40 | 136.2 | 252 | 142 | 136
3:50 | 136.5 | 253 | 142 | 136
4:00 | 136.8 | 254 | 142 | 136
4:10 | 136.9 | 253 | 142 | 136
4:20 | 137.5 | 252 | 142 | 136
4:30 | 137.9 | 253 | 142 | 136
4:40 | 138 | 250 | 142 | 136
4:50 | 138.2 | 252 | 142 | 136
5:00 | 138.5 | 253 | 142 | 136
5:10 | 138.5 | 254 | 142 | 136
5:20 | 138.6 | 253 | 142 | 136
5:30 | 138.7 | 252 | 142 | 136
5:40 | 138.8 | 253 | 142 | 136
5:50 | 140 | 250 | 142 | 136
6:00 | 140.2 | 252 | 142 | 136
6:10 | 141 | 253 | 142 | 136
6:20 | 141.5 | 254 | 142 | 136
6:30 | 141 | 253 | 142 | 136
6:40 | 139.5 | 252 | 142 | 136
6:50 | 139.4 | 253 | 142 | 136
7:00 | 139.3 | 250 | 142 | 136
7:10 | 139.2 | 252 | 142 | 136
7:20 | 138.9 | 253 | 142 | 136
7:30 | 138.5 | 254 | 142 | 136
7:40 | 138.3 | 253 | 142 | 136
7:50 | 138.1 | 252 | 142 | 136
8:00 | 137.5 | 253 | 142 | 136
8:10 | 137.3 | 250 | 142 | 136
8:20 | 137.1 | 252 | 142 | 136
8:30 | 136.4 | 253 | 142 | 136
8:40 | 136.3 | 254 | 142 | 136
8:50 | 136.2 | 253 | 142 | 136
9:00 | 136.5 | 252 | 142 | 136
9:10 | 136.8 | 253 | 142 | 136
9:20 | 136.9 | 250 | 142 | 136
9:30 | 137.5 | 252 | 142 | 136
9:40 | 137.9 | 253 | 142 | 136
9:50 | 138 | 254 | 142 | 136
10:00 | 138.2 | 253 | 142 | 136
10:10 | 138.5 | 252 | 142 | 136
10:20 | 138.5 | 253 | 142 | 136
10:30 | 138.6 | 250 | 142 | 136
10:40 | 138.7 | 252 | 142 | 136
10:50 | 138.8 | 253 | 142 | 136
11:00 | 140 | 254 | 142 | 136
11:10 | 140.2 | 253 | 142 | 136
11:20 | 141 | 252 | 142 | 136
11:30 | 141.5 | 253 | 142 | 136
11:40 | 141 | 250 | 142 | 136
11:50 | 139.5 | 252 | 142 | 136
12:00 | 139.4 | 253 | 142 | 136
12:10 | 139.3 | 254 | 142 | 136
12:20 | 139.2 | 253 | 142 | 136
12:30 | 138.9 | 252 | 142 | 136
12:40 | 138.5 | 253 | 142 | 136
12:50 | 138.3 | 250 | 142 | 136
13:00 | 138.1 | 252 | 142 | 136
13:10 | 137.5 | 253 | 142 | 136
13:20 | 137.3 | 254 | 142 | 136
13:30 | 137.1 | 253 | 142 | 136
13:40 | 136.4 | 252 | 142 | 136
13:50 | 136.3 | 253 | 142 | 136
14:00 | 136.2 | 250 | 142 | 136
14:10 | 136.5 | 252 | 142 | 136
14:20 | 136.8 | 253 | 142 | 136
14:30 | 136.9 | 254 | 142 | 136
14:40 | 137.5 | 253 | 142 | 136
14:50 | 137.9 | 252 | 142 | 136
15:00 | 138 | 253 | 142 | 136
15:10 | 138.2 | 250 | 142 | 136
15:20 | 138.5 | 252 | 142 | 136
15:30 | 138.5 | 253 | 142 | 136
15:40 | 138.6 | 254 | 142 | 136
15:50 | 138.7 | 253 | 142 | 136
16:00 | 138.8 | 252 | 142 | 136
16:10 | 140 | 253 | 142 | 136
16:20 | 140.2 | 250 | 142 | 136
16:30 | 141 | 252 | 142 | 136
16:40 | 141.5 | 253 | 142 | 136
16:50 | 141 | 254 | 142 | 136
17:00 | 139.5 | 253 | 142 | 136
17:10 | 139.4 | 252 | 142 | 136
17:20 | 139.3 | 253 | 142 | 136
17:30 | 139.2 | 250 | 142 | 136
17:40 | 138.9 | 252 | 142 | 136
17:50 | 138.5 | 253 | 142 | 136
18:00 | 138.3 | 254 | 142 | 136
18:10 | 138.1 | 253 | 142 | 136
18:20 | 137.5 | 252 | 142 | 136
18:30 | 137.3 | 253 | 142 | 136
18:40 | 137.1 | 250 | 142 | 136
18:50 | 136.4 | 252 | 142 | 136
19:00 | 136.3 | 253 | 142 | 136
19:10 | 136.2 | 254 | 142 | 136
19:20 | 136.5 | 253 | 142 | 136
19:30 | 136.8 | 252 | 142 | 136
19:40 | 136.9 | 253 | 142 | 136
19:50 | 137.5 | 250 | 142 | 136
20:00 | 137.9 | 252 | 142 | 136
20:10 | 138 | 253 | 142 | 136
20:20 | 138.2 | 254 | 142 | 136
20:30 | 138.5 | 253 | 142 | 136
20:40 | 138.5 | 252 | 142 | 136
20:50 | 138.6 | 253 | 142 | 136
21:00 | 138.7 | 250 | 142 | 136
21:10 | 138.8 | 252 | 142 | 136
21:20 | 140 | 253 | 142 | 136
21:30 | 140.2 | 254 | 142 | 136
21:40 | 141 | 253 | 142 | 136
21:50 | 141.5 | 252 | 142 | 136
22:00 | 141 | 253 | 142 | 136
22:10 | 139.5 | 250 | 142 | 136
22:20 | 139.4 | 252 | 142 | 136
22:30 | 139.3 | 253 | 142 | 136
22:40 | 139.2 | 254 | 142 | 136
22:50 | 138.9 | 253 | 142 | 136
23:00 | 138.5 | 252 | 142 | 136
23:10 | 138.3 | 253 | 142 | 136
23:20 | 138.1 | 250 | 142 | 136
23:30 | 137.5 | 252 | 142 | 136
23:40 | 137.3 | 253 | 142 | 136
23:50 | 137.1 | 254 | 142 | 136
Minimum | 136.2 |  |  | 136
Maximum | 145 |  | 142